SECTION 02530 - SANITARY SEWERAGE

- GENERAL

      - SECTION REQUIREMENTS

        - Submittals:  Coordination Drawings showing piping profiles and elevations at a horizontal scale of 1 inch equals 50 feet (1:500) and a vertical scale of 1 inch equals 5 feet (1:50).  Indicate underground structures and show pipe types, sizes, and materials and elevations of other utilities crossing system piping.

- PRODUCTS

      - PIPE AND FITTINGS

        - Hub-and-Spigot, Cast-Iron Soil Pipe and Fittings:  ASTM A 74 Service class, gray cast iron, for gasketed joints.  Include ASTM C 564 rubber, compression-type gaskets.

        - PVC Sewer Pipe and Fittings:  ASTM D 3034, SDR 35, for gasketed joints.  Include ASTM F 477 elastomeric seals.

        - Protective Coatings:  Coal-tar epoxy; 15-mil (0.38-mm) minimum thickness, factory or field applied to exterior and interior surfaces of concrete manholes and entire surfaces of manhole frames and covers.

        - Gray-Iron Cleanouts:  ASME A112.36.2M, round, gray-iron housing with clamping device and round, secured, scoriated, gray-iron cover.  Include gray-iron ferrule with inside calk or spigot connection and countersunk, tapered-thread, brass closure plug.  Use units with heavy-duty top-loading classification in vehicle-traffic service areas and medium-duty in paved foot-traffic areas.

- EXECUTION

      - INSTALLATION

        - Install piping beginning at low point, true to grades and alignment indicated with unbroken continuity of invert.  Place bell ends of piping facing upstream.

        - Install piping pitched down in direction of flow, at minimum slope of 2 percent, unless otherwise indicated, with 36-inch (1000-mm) minimum cover.

        - Use manholes for changes in direction, unless fittings are indicated.  Use fittings for branch connections, unless direct tap into existing sewer is indicated.

        - Install hub-and-spigot, cast-iron soil pipe and fittings with rubber gaskets according to CISPI's "Cast Iron Soil Pipe and Fittings Handbook," Volume I.  Use gaskets that match class of pipe and fittings.

        - Install PVC pipe and gasketed fittings with gaskets according to ASTM D 2321.

      - FIELD QUALITY CONTROL

        - Clean and inspect piping and structures.

        - Test complete piping according to authorities having jurisdiction.

END OF SECTION 02530