SECTION 15430 – PLUMBING EQUIPMENT

- GENERAL

      - SECTION REQUIREMENTS

        - Submittals:  Product Data.

        - Instantaneous Water Heaters:  Bear AGA certification label.

        - Tankless LPG water heaters

- 1.2       	QUALITY ASSURANCE

- A.       Manufacturer Qualifications: Company specializing in manufacturing the type of products speci

- fied in this section, with minimum of three years experience.

- B.        Identification:   Provide devices  with manufactures name, model number, and rating/capacity

- identified by permanently attached label

- C.        Standards:   Ensure products and installation of specified products are in conformance with

- recommendations and requirements of the American Society of Mechanical Engineers, and

- Underwriters  Laboritories.

- PRODUCTS

      - WATER HEATERS, GENERAL

        - Unit shall be a one piece compact design suitable for an undersink mounting location, and shall be demand only (no storage) UL listed design.

        - Element: Nichol Chrome element with replaceable cartridge.

        - Controls: Heating element shall activate on demand via flow switch. Flow switch shall be factory set to activate element at a flow rate which limits the temperature rise to a maximum of 55 degrees farenheit.

2.2            TANKLESS WATER HEATERS - LPG

- Approved Manufacturers.

  - The basis of design is Rinnai Corporation.  The following manufacturers are approved equal provided they can meet the performance, material and operational features of the basis for design equipment.

  - Rheem

  - Noritz

- Units shall be NSF and ASME approved for the application.

- The water heater shall provide temperature controlled continuous water flow.

- The unit shall incorporate a digital display and control panel.

- Operation shall be forced combustion using LP gas.  The unit shall incorporate venting of the products of combustion.

- The unit shall suitable for outdoor installation with zero clearance of the back of the unit to the exterior wall construction.  All components shall be weather protected.

- Safety Features

  - Overheat: The appliance will automatically shut down when the appliance exceeds a predetermined temperature.

  - Flame Failure: The appliance will automatically shut down if the burner flame is extinguished.

  - Power Failure: The appliance will cut off the gas if it loses electrical power.

  - Power Surge Fuse: A glass fuse protects against over current. If the fuse blows then all indicator lamps will be off.
Fusible Link: In case the overheat feature does not prevent the temperature from rising then the fusible link will break shutting off the appliance.

- Accessories & Options

  - Temperature controller MC-91.

- Warranty:  5 years parts and 1 year labor.

- EXECUTION

      - INSTALLATION

        - Install water heaters in accordance with manufacturer’s instructions and to UL and other listing requirements.

        - Coordinate with plumbing piping and related electrical work to achieve operating system.

END OF SECTION 15430