SECTION 16070 - HANGERS AND SUPPORTS

PARTI GENERAL

1.1 SECTION INCLUDES

- Conduit and equipment supports.

- Anchors and fasteners.

1.2 REFERENCES

- NECA 1 - Standard Practices for Good Workmanship in Electrical Contracting; National Electrical

Contractors Association; 2006.

- NFPA 70 - National Electrical Code, NFPA (edition adopted by Authority Having Jurisdiction).

1.3 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Products: listed and classified by Underwriters Laboratories Inc. as suitable for the purpose specified

and indicated.

PART 2 PRODUCTS

2.1 MATERIALS

- Hangers, Supports, Anchors, and Fasteners· General: corrosion-resistant materials of size and type

adequate to carry the loads of equipment and conduit, including weight of wire in conduit.

- Supports: Fabricated of structural steel or formed steel members; galvanized.

- Anchors and Fasteners:

- Do not use powder-actuated anchors. spring clips, or beam clamps.

- Concrete Structural Elements: Use precast inserts, expansion anchors, powder-actuated anchors, or preset Inserts.

- Steel Structural Elements: Use beam clamps, steel spring clips, steel ramset fasteners, or

welded fasteners.

- Concrete Surfaces: Use self-drilling anchors or expansion anchors.

- Hollow Masonry, Plaster, and Gypsum Board Partitions: Use toggle bolts or hollow wall

fasteners.

- Solid Masonry Walls: Use expansion anchors or preset inserts.

- Sheet Metal: Use sheet metal screws.

- Wood Elements: Use wood screws.

PART 3 EXECUTION

3.1 INSTALLATION

- Install hangers and supports as required 10 adequately and securely support electrical system

components, in a neat and workmanlike manner, as specified in NECA 1.

- Do not fasten supports to pipes, ducts, mechanical equipment, or conduit.

- Obtain permission from GOVERNMENT before drilling or cutting structural members.

- Rigidly weld support members or use hexagon-head bolls to present neat appearance with adequate

strength and rigidity. Use spring lock washers under all nuts.

- Install surface-mounted cabinets and panel boards with minimum of four anchors.

- In wet and damp locations use steel channel supports to stand cabinets and panelboards 1 inch (25

mm) off wall.

- Use sheet metal channel to bridge studs above and below cabinets and panelboards recessed in

hollow partitions.

END OF SECTION