INSTALLATION

15820 - 3

3. Externally visible position indicators with wing nut lock device.

C. Single Blade Manual Volume Dampers

1. Round:  Ruskin MDRS25 or equal.

2.  Rectangular:  Ruskin MD25 or equal.

D. Splitter Dampers:

E. Opposed blade balancing dampers shall be 16 gauge minimum galvanized steel with zinc-plated

hardware and bronze or nylon bearings.  Blades shall not be over 8” wide.  Maximum leakage shall be

less than 1% at a static pressure of 4” w.g.

PART 3 EXECUTION

3.1

A. Install accessories in accordance with manufacturer’s instructions, NFPA 90A, and follow SMACNA

HVAC Duct Construction Standards.  Refer to Section 15810 for duct construction and pressure class.

B. Provide backdraft dampers on exhaust fans or exhaust ducts where indicated.

C. Provide duct test holes where required for testing and balancing purposes.

D. Provide ire dampers at locations indicated, where ducts and outlets pass through ire rated

components, and where required by authorities having jurisdiction.  Prior to bidding, review

architectural plans for last minute changes on locations of ire rated walls.  Install with required

perimeter mounting angles, sleeves, breakaway duct connection, corrosion resistant springs,

bearings, bushings and hinges.

E. Demonstrate re-setting of ire dampers to Owner’s representative.

F. At fans and motorized equipment associated with ducts, provide lexible duct connections immediately

adjacent to the equipment.

G. Provide balancing dampers at points on supply, return, and exhaust systems where branches are

taken from larger ducts as required for air balancing.  Install minimum 2 duct widths from duct take-off.

H. Use splitter dampers only where indicated.

I. Provide opposed blade dampers as necessary to supplement multiple speed air handling units to

obtain scheduled total airlow.

J. Provide single blade balancing dampers at duct take-off to diffusers, grilles, and registers, unless

included in diffuser or register schedule.  If impractical due to space limitations, an opposed blade

damper shall be provided as an accessory to the diffuser, grille or register.

END OF SECTION

DUCT ACCESSORIES

This Document has been created with a trial version of deskUNPDF.  To

purchase a copy of deskUNPDF and remove the trial restrictions, please visit

www.docudesk.com or email sales@docudesk.com for assistance.