SECTION 16140 - WIRING DEVICES

PART1 GENERAL

1.1 SECTION INCLUDES

- Wall switches.

- Wall dimmers.

- Receptacles.

- Device plates and decorative box covers.

1.2 REFERENCES

- NECA 1 - Standard Practices for Good Workmanship in Electrical Contracting; National Electrical

Contractors Association; 2006.

- NEMA WD 1 - General Color Requirements for Wiring Devices; National Electrical Manufacturers

Association; 1999 (R 2005)_

- NEMA WO 6 - Wiring Device -- Dimensional Requirements; National Electrical Manufacturers

Association; 2002 (R200B)_

- NFPA 70 - National Electrical Code, National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

1.3 SUBMITIALS

- See Section 01300 . Administrative Requirements, for submittal procedures.

- Product Data: Provide manufacturer's catalog information showing dimensions, colors, and

configurations.

1.4 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this

section with minimum three years documented experience.

- Products: Provide products listed and classified by Underwriters Laboratories Inc. as suitable for the

purpose specified and indicated.

PART 2 PRODUCTS

2.1 MANUFACTURERS.

- All devices shall be specification grade and shall be the product of one manufacturer throughout the

project except as otherwise noted.

2.2 WALL SWITCHES

- Wall Switches: NEMA WD 1, Heavy Duly, AC only general-use snap switch, quiet type with side wire

terminals. Switches shall be single or multi-pole as indicated on the Drawings. Provide Leviton

Decora Switches, or equal, if indicated on drawings.

- Body and Handle: plastic with toggle handle unless otherwise indicated. Color shall be as

determined by GOVERNMENT.

- Ratings:

  - Voltage: 120-277 volts, AC.

  - Current: 20 amperes.

2.3 WALL DIMMERS

- Wall Dimmers: Semiconductor dimmer for incandescent lamps, Type as indicated on drawings,

complying with NEMA WD 6 and WD 1.

  - Body and Handle: plastic with linear slide unless otherwise indicated. Color as determined by

GOVERNMENT.

  - Power Rating: Match load shown on drawings; 600 watts minimum.

- Accessory Wall Switches: Match dimmer appearance.

2.4 RECEPTACLES

- Receptacles: Heavy duty, complying with NEMA WD 6 and WD 1

  - Duplex receptacles shall be straight blade, grounding type, with side wiring terminals.

Conductors shall be connected to all receptacles using screws (not spring connectors).

  - Device Body: plastic unless otherwise indicated. Color as determined by GOVERNMENT.

  - Configuration: NEMA WD 6, type as specified and indicated.

- Convenience Receptacles: Type 5-20.

- Duplex Convenience Receptacles.

- GFCI Receptacles: Convenience receptacle with integral ground fault circuit interrupter to meet

regulatory requirements. Also, provide GFCI receptacles where indicated. GFCI type receptacles

shall have "test" and "reset" buttons.

- Weather proof receptacles shall be in a cast metal box with gasketed, weatherproof, cast-metal cover

plate and gasketed cap over each receptacle opening. Provide caps with a spring-hinged flap.

Weatherproof receptacles shall be UL listed for use in wet locations with plug in use and shall be

GFCI rated.

- Floor-mounted receptacles shall have a brass plate and cover, unless noted otherwise.

- Special purpose outlets shall be as indicated on the Drawings and have matching cover plates.

2.5 WALL PLATES

- Decorative Cover Plates: smooth plastic unless otherwise indicated on drawings. Color as

determined by GOVERNMENT.

- Weatherproof Cover Plates: Gasketed cast metal with hinged.

PART3 EXECUTION

3.1 EXAMINATION

- Verify that outlet boxes are installed at proper height.

- Verily that wall openings are neatly cut and will be completely covered by wall plates.

- Verily that floor boxes are adjusted properly.

- Verify that branch Circuit wiring installation is completed, tested, and ready for connection to wiring

devices.

3.2 PREPARATION

- Provide extension rings to bring outlet boxes flush with finished surface.

- Clean debris from outlet boxes.

3.3 INSTALLATION

- Install securely, in a neat and workmanlike manner, as specified in NECA 1.

- Install devices plumb and level.

- Install switches with OFF position down.

- Install wall dimmers to achieve full rating specified and indicated after derating for ganging as

instructed by manufacturer. For dimmers associated with electronic ballasts, provide separate box

and plate (do not combine with other switches).

- Do not share neutral conductor on load side of dimmers.

- Install receptacles with grounding pole on bottom.

- Connect wiring device grounding terminal to outlet box with bonding jumper.

- Do not cut cover plate.

- Install decorative plates on switch, receptacle, and blank outlets in finished areas.

- Connect wiring devices by wrapping conductor around screw terminal.

3.4 INTERFACE WITH OTHER PRODUCTS

- Install wall switch 48 inches (1.2 m) (10 center of switch) above finished floor, unless otherwise

indicated. Conform to all ADA requirements.

- Install convenience receptacle 18 inches (450 mm) above finished floor, unless otherwise indicated.

- Install convenience receptacle with bottom 6 inches (150 mm) above counter.

- Install dimmer 48 inches (1.2 m) (to center of switch) above finished floor, unless otherwise indicated.

Conform to all ADA requirements.

3.5 FIELD QUALITY CONTROL

- Perform field inspection, testing, and adjusting in accordance with Section 01400.

- Inspect each wiring device for defects.

- Operate each wall switch with circuit energized and verify proper operation.

- Verify that each receptacle device is energized.

- Test each receptacle device for proper polarity.

- Test each GFCI receptacle device for proper operation.

3.6 ADJUSTING

- Adjust devices and wall plates to be flush and level.

3.7 CLEANING

- Clean exposed surfaces to remove splatters and restore finish.

END OF SECTION