SECTION 16138 - BOXES

PARTI GENERAL

1.1 SECTION INCLUDES

- Wall and ceiling outlet boxes.

- Floor boxes.

- Pull and junction boxes.

1.2 REFERENCES

- NECA 1 . Standard Practices for Good Workmanship in Electrical Contracting; National Electrical

Contractors Association; 2006.

- NEMA FB 1 . Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit, Electrical Metallic Tubing,

and Cable; National Electrical Manufacturers Association; 2007.

- NEMA OS 1 . Sheet Steel Outlet Boxes, Device Boxes, Covers, and Box Supports; National Electrical

Manufacturers Association; 2003.

- NEMA 250 · Enclosures for Electrical Equipment (1000 Volts Maximum); National Electrical

Manufacturers Association; 2008.

- NFPA 70 - National Electrical Code, National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

1.3 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Products: Provide products listed and classified by Under Writers Laboratories Inc., as suitable for the

purpose specified and indicated.

PART 2 PRODUCTS

2.1 OUTLET BOXES

- Sheet Metal Outlet Boxes: NEMA OS 1, galvanized steel boxes

  - Luminaire and Equipment Supporting Boxes: Rated for weight of equipment supported; include

1/2 inch (13 mm) male fixture studs where required.

  - Concrete Ceiling Boxes: Concrete type.

  - Boxes for installation in concrete block wall construction shall be gang type, 3-1 /2' deep for

switch devices and 4" square by 1-1/2" deep, with 1·1/4" single and two gang square corner

extension covers for receptacle and junction purposes. Boxes for installation in brick wall

construction shall be gang type, 3-1/2" deep. Boxes installed in plastered walls shall be 4"

square by 1-1 /2" deep, with ¾”· single and two gang plaster covers. All boxes shall have internal

mounting ears or threaded tappings.

- Cast Boxes: NEMA FB 1, Type FD. aluminum. Provide gasketed cover by box manufacturer.

Provide threaded hubs.

- Wall Plates for Finished Areas: As specified in Section 16140.

2.2 FLOOR BOXES

- Floor Boxes: NEMA OS 1, fully adjustable, 1-1/2 inches (38 mm) deep.

- Material: Cast metal.

2.3 PULL AND JUNCTION BOXES

- Sheet Metal Boxes: NEMA OS 1, galvanized steel. Boxes shall be 1 1/2" deep minimum. Boxes to

which fixtures are installed shall have studs and straps to support fixture weight.

- Pull and junction boxes shall be constructed of code gauge galvanized sheet steel and fitted with

screw covers held in place with corrosion resistant machine screws.

- Provide boxes where noted on Drawings or where necessary to facilitate conductor pulling and

splicing. Splicing of conductors is to be avoided as much as possible with continuous lengths being

preferred. Box sizes shall conform to sizes required by NEC or as indicated on the Drawings (if larger

than required by NEC).

- Surface Mounted Cast Metal Box: NEMA 250, Type 4; flat-flanged, surface mounted junction box:

  - Material: Galvanized cast iron.

  - Cover: Furnish with ground flange, neoprene gasket, and stainless steel cover screws.

- In-Ground Cast Metal Box: NEMA 250, Type 6, outside flanged, recessed cover box tor flush

mounting:

  - Material: Galvanized cast iron.

  - Cover: Smooth cover with neoprene gasket and stainless steel cover screws.

- Fiberglass Handholes: Die molded glass fiber hand holes:

  - Cable Entrance: Pre-cut 6 x 6 inch (150 x 150 mm) cable entrance at center bottom of each

side.

  - Cover: Glass fiber weatherproof cover with nonskid finish.

PART 3 EXECUTION

3.1 EXAMINATION

- Verify locations of floor boxes and outlets in offices and work areas prior to rough-in.

3.2 INSTALLATION

- Install boxes securely, in a neat and workmanlike manner, as specified in NECA 1.

- Install in locations as shown on Drawings, and as required for splices, taps, wire pulling, equipment

connections, and as required by NFPA 70.

- Coordinate installation of outlet boxes for equipment connected under Section 16155.

- Electrical boxes are shown on Drawings in approximate locations unless dimensioned.

1. Adjust box locations up to 10 feet (3 m) if required to accommodate intended purpose.

- Orient boxes to accommodate wiring devices oriented as specified in Section 16140.

- Maintain headroom and present neat mechanical appearance.

- lnstall pull boxes and junction boxes above accessible ceilings and in unfinished areas only.

- Inaccessible Ceiling Areas: Install outlet and junction boxes no more than 6 inches (150 mm) from

ceiling access panel or from removable recessed luminaire.

- Install boxes to preserve fire resistance rating of partitions and other elements.

- Coordinate mounting heights and locations of outlets mounted above counters, benches, and

backsplashes.

- Locate outlet boxes to allow luminaires positioned as shown on reflected ceiling plan.

- Align adjacent wall mounted outlet boxes for switches, thermostats, and similar devices.

- Use flush mounting outlet box in finished areas.

- Locate flush mounting box in masonry wall to require cutting of masonry unit comer only. Coordinate

masonry cutting to achieve neat opening.

- Do not install flush mounting box back-to-back in walls; provide minimum 6 inches (150 mm)

separation. Provide minimum 24 inches (600 mm) separation in acoustic rated walls.

- Secure flush mounting box to interior wall and partition studs. Accurately position to allow for surface

finish thickness.

- Use stamped steel bridges 10 fasten flush mounting outlet box between studs.

- Install flush mounting box without damaging wall insulation or reducing its effectiveness.

- Use adjustable steel channel fasteners for hung ceiling outlet box.

- Do not fasten boxes to ceiling support wires.

- Support boxes independently of conduit, except cast box that is connected to two rigid metal conduits

both supported within 12 inches (305 mm) 01 box.

- Use gang box where more than one device is mounted together. Do not use sectional box.

- Use gang box with plaster ring for single device outlets.

- Use cast outlet box in exterior locations exposed to the weather and wet locations.

- Use cast floor boxes for installations in slab on grade; formed steel boxes are acceptable for other

installations.

- Set floor boxes level.

- Large Pull Boxes: Use hinged enclosure in interior dry locations, surface-mounted cast metal box in

other locations.

3.3 ADJUSTING

- Adjust floor boxes flush with finish flooring material.

- Adjust flush-mounting outlets to make front flush with finished wall material.

- Install knockout closures in unused box openings.

3.4 CLEANING

- Clean interior of boxes to remove dust, debris, and other material.

- Clean exposed surfaces and restore finish.

END OF SECTION