SECTION 02510 - WATER DISTRIBUTION

- GENERAL

      - SECTION REQUIREMENTS

        - Summary:  This Section includes water system piping for potable-water service, outside the building.

Retain subparagraph below where appropriate.

          - This Section does not include tapping of utility company water main by utility company and charged directly to Owner.

        - Unless otherwise indicated, the minimum pressure requirements for water piping are 150 psig (1035 kPa) for all underground piping, except 200 psig (1380 kPa) for piping downstream from fire department connections.

        - Comply with NFPA 24, "Standard for the Installation of Private Fire Service Mains and Their Appurtenances," for materials, installations, tests, and flushing.

Delete paragraph below if PVC pipe is not used.

        - Comply with ASTM F 645, "Guide for Selection, Design, and Installation of Thermoplastic Water Pressure Piping Systems."

        - Comply with NFPA 70.

- PRODUCTS

      - COPPER TUBE AND FITTINGS

        - Copper Tube:  ASTM B 88 (ASTM B 88M), seamless water tube, annealed temper.

        - Copper Fittings:  ASME B16.22; wrought-copper, solder-joint pressure type.

        - Cast-Copper-Alloy Flanges:  ASME B16.24, Class 150 or 300, as required for system operating pressure.

        - Brazing Filler Metals:  AWS A5.8, BCuP Series.

        - Solder Filler Metal:  ASTM B 32, Alloy Sn95, Alloy Sn94, or Alloy E, with 0.10 percent maximum lead content.

      - DUCTILE-IRON PIPE AND FITTINGS

        - Ductile-Iron Pipe:  mechanical-joint pipe, AWWA C151, Classes 150, 200, and 250; with AWWA C104 cement-mortar, seal-coated lining; AWWA C111 glands, bolts and nuts, and rubber gaskets.

        - Ductile-Iron Pipe Fittings:  AWWA C110 ductile iron or cast iron, 250-psig (1725-kPa) minimum pressure rating, and AWWA C104 cement-mortar lining.

        - Ductile-Iron, Flexible Expansion Joints:  Compound fitting with combination of flanged and mechanical-joint ends complying with AWWA C110 or AWWA C153.

        - Ductile-Iron Pipe and Ductile- or Cast-Iron Fittings:  The following materials apply:

          - Push-on Joints:  AWWA C111 rubber gaskets and lubricant.

          - Mechanical Joints:  AWWA C111 ductile- or gray-iron glands, high-strength steel bolts and nuts, and rubber gaskets.

          - Flanged Joints:  AWWA C115 ductile- or gray-iron pipe flanges, rubber gaskets, and high-strength steel bolts and nuts.

      - PVC PIPE AND FITTINGS

        - PVC Plastic Pipe:  ASTM D 1785, with marking "NSF-pw" according to NSF 14.

        - PVC Plastic, Fire-Service Pipe:  UL 1285 and AWWA C900.  Include elastomeric seal according to ASTM F 477.

        - PVC Plastic, Socket Fittings:  ASTM D 2467, Schedule 80.

        - PVC Plastic Fittings:  UL 1285 and AWWA C907, Class 150.  Include elastomeric seals according to ASTM F 477.

        - Primers for PVC Piping Solvent-Cement Joints:  ASTM F 656.

        - Solvent Cement for PVC Piping Solvent-Cement Joints:  ASTM D 2564.

      - VALVES

        - Nonrising-Stem, Resilient-Seated Gate Valves, NPS 3 (DN80) and Larger:  AWWA C509, gray- or ductile-iron body and bonnet; with bronze or gray- or ductile-iron gate, resilient seats, bronze stem, and stem nut.  Include 200-psig (1380-kPa) minimum working-pressure design, interior coating according to AWWA C550, and push-on- or mechanical-joint ends.

Paragraph below is for use with indicator post.

        - Nonrising-Stem Gate Valves:  UL 262, FM-approved, iron body and bonnet with flange for indicator post, bronze seating material, inside screw, 175-psig (1200-kPa) working pressure, and mechanical-joint ends.  Provide with flanged ends for pit installation.

        - Valve Boxes:  Cast-iron box with top section and cover with lettering "WATER," bottom section with base of size to fit over valve and barrel approximately 5 inches (125 mm) in diameter, and adjustable cast-iron extension of length required for depth of bury of valve.

        - Indicator Posts:  UL 789, FM-approved, vertical-type, cast-iron body with operating wrench, extension rod, and adjustable cast-iron barrel of length required for depth of bury of valve.

        - Curb Stops:  Bronze body, ground key plug or ball, and wide tee head, with inlet and outlet to match service piping material.

      - SPECIALTIES

        - Fire Hydrants:  Cast-iron body, compression-type valve, opening against pressure and closing with pressure, NPS 6 (DN150) mechanical-joint inlet, 150-psig (1035-kPa) working pressure.  NFPA 1963, with external hose thread used by local fire department.  Include cast-iron caps with steel chains.

        - Exposed, Sidewalk Fire Department Connections:  UL 405 cast-brass body, with thread inlets according to NFPA 1963 and matching local fire department hose threads, and threaded NPS bottom outlet.

        - ASSE standard backflow preventers, of size indicated for maximum flow rate and maximum pressure loss indicated.

        - Hose-Connection Vacuum Breakers:  ASSE 1011, nickel plated, with nonremovable and manual drain features, and ASME B1.20.7, 3/4-11.5NH threads for garden hose on outlet.  Units attached to rough-bronze-finish hose connections may be rough bronze.

        - Water-Flow Indicators:  Vane-type water-flow detector, rated for 250-psig (1725-kPa) working pressure; designed for horizontal or vertical installation; with 2 SPDT circuit switches to provide isolated alarm and auxiliary contacts, 7 A 125-V ac and 0.25 A 24-V dc; complete with factory-set, field-adjustable retard element to prevent false signals and tamperproof cover that sends signal when cover is removed.

        - Plastic Underground Warning Tapes:  Polyethylene plastic tape, 6 inches (150 mm) wide by 4 mils (0.1 mm) thick, solid blue in color with metallic core and continuously printed black-letter caption "CAUTION--WATER LINE BURIED BELOW."

- EXECUTION

      - INSTALLATION

        - Connect water system piping and water-supply source and building water-distribution and fire-protection systems at the building wall in locations and pipe sizes indicated.

        - Install restrained joints for buried piping within 60 inches (1500 mm) of building.  Use restrained-joint pipe and fittings, thrust blocks, anchors, tie rods and clamps, and other supports at vertical and horizontal offsets.

        - Install fittings for changes in direction and branch connections.

        - Install ductile-iron pipe and ductile- and cast-iron fittings according to AWWA C600.

        - Install copper tube and fittings according to CDA's "Copper Tube Handbook."

        - Install AWWA PVC plastic pipe according to AWWA M23 and ASTM F 645.

        - Bury piping at minimum depth of 36 inches (1000 mm) below finished grade and at least 18 inches (500 mm) below average local frost depth.

        - Clean and disinfect water distribution piping according to authorities having jurisdiction.

END OF SECTION 02510