SECTION 16443 - PANELBOARDS

PART1 GENERAL

1.1 SECTION INCLUDES

- Power distribution panelboards.

- Lighting and appliance panelboards.

1.2 REFERENCES

- NECA 1 - Standard Practices for Good Workmanship in Electrical Contracting; National Electrical

Contractors Association; 2006.

- NEMA AS 1 . Molded Case Circuit Breakers and Molded Case Switches; National Electrical

Manufacturers Association; 1993.

- NEMA PB 1 - Panelboards; National Electrical Manufacturers Association; 2006.

- NEMA PB 1.1 – General Instructions for Proper Installation, Operation and Maintenance of

Panelboards Rated 600 Volts or Less; National Electrical Manufacturers Association; 2007.

- NETA STD ATS· Acceptance Testing Specifications for Electrical Power Distribution Equipment and

Systems; International Electrical Testing Association; 2007.

- NFPA 70 - National Electrical Code, National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

1.3 SUBMITIALS

- Shop Drawings: Indicate outline and support point dimensions, voltage, main bus ampacity,

integrated short circuit ampere rating, circuit breaker and fusible switch arrangement and sizes.

- Provide catalog data for Transient Voltage Surge Suppression Devices.

1.4 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this

section with minimum three years documented experience.

- Products: Listed and classified by Underwriters laboratories Inc. as suitable for the purpose specified

and indicated.

PART 2 PRODUCTS

2.1 MANUFACTURERS

- Basis of Design: Square D; www.squared.com.

2.2 POWER DISTRIBUTION PANELBOARDS

- Description: NEMA PB 1, circuit breaker type.

- Panelboard Bus: Copper, ratings as indicated. Provide copper ground bus in each panelboard.

- Minimum integrated short circuit rating: As indicated.

- Molded Case Circuit Breakers: NEMA AS 1, bolt-on circuit breakers with integral thermal and

instantaneous magnetic trip in each pole. Provide circuit breakers UL listed as Type HACR for air

conditioning equipment branch circuits.

- Enclosure: NEMA PB 1, enclosure type as indicated on drawings.

- Cabinet Front: Surface type, fastened with concealed trim clamps, hinged door with flush lock, metal

directory frame, finished in manufacturer's standard gray enamel.

- Provide blank covers as necessary to cover unused spaces in panelboard. Blank covers shall be

manufactured by the manufacturer of the panelboard and intended for this purpose.

2.3 LIGHTING AND APPLIANCE PANELBOARDS

- Description: NEMA PB1 , circuit breaker type, lighting and appliance branch circuit panelboard.

- Panelboard Bus: Copper, ratings as indicated. Provide copper ground bus in each panelboard; provide insulated ground bus where scheduled.

- Minimum Integrated Short Circuit Rating: As indicated.

- Molded Case Circuit Breakers: NEMA AB 1, bolt-on type thermal magnetic trip circuit breakers, with

common trip handle for all poles. Plug-in circuit breakers are not acceptable.

- Type HACR for air conditioning equipment circuits.

- Do not use tandem circuit breakers.

- Enclosure: NEMA PB 1, as indicated on drawings.

- Cabinet Box: 6 inches (153 mm) deep, 20 inches (508 mm) wide for 240 volts and less panelboards,

20 inches (508 mm) wide for 480 volt panelboards.

- Cabinet Front: Flush or Surface Mount as indicated on drawings. Cabinet front with concealed trim

clamps, concealed hinge, metal directory frame, and flush lock all keyed alike. Finish in

manufacturers standard gray enamel.

- Provide blank covers as necessary to cover unused spaces in panelboard. Blank covers shall be

manufactured by the manufacturer of the panelboard and intended for this purpose.

2.4 TRANSIENT VOLTAGE SURGE SUPPRESSION.

- Provide Transient Voltage Surge Suppression (TVSS) where indicated on the Drawings . The TVSS

device shall have a surge current rating as indicated on the drawings and shall be service rated,

where required. Maximum UL1449 2nd edition clamping voltage (C3, 20kv, 10ka, combination wave)

shall be 1,150 Volts line to neutral and 1,950 Volts line to line for 480 Volt systems and 450 Volts line

to neutral and 800 Volts line to line for 208 or 240 Volt systems. The TVSS device shall be UL listed

and shall meet all criteria of UL 1449, current edition. Additionally, the device shall contain visual fault

indication. The TVSS device shall be installed in accordance with manufacturer's recommendations,

and shall be installed as close as possible to the incoming panel feeder using a spare circuit breaker

(confirm size of circuit breaker with TVSS manufacturer). Provide integral TVSS when required in

design drawings. If installed at a enclosed main circuit breaker, provide over-current protection and

disconnect.

PART 3 EXECUTION

3.1 INSTALLATION

- Install panelboards in accordance with NEMA PB 1.1 and NECA 1.

- Install panelboards plumb. Install recessed panelboards flush with wall finishes.

- Height: 6 feet (1800 mm) to top of panelboard; install panelboards taller than 6 feet (1800 mm) with

bottom no more than 4 inches (100 mm) above floor.

- Provide filler plates for unused spaces in panelboards.

- Provide typed circuit directory for each branch circuit panelboard. Revise directory to reflect

circuiting changes required to balance phase loads.

- Provide engraved plastic nameplates under the provisions of Section 16075

- For panels installed flush in finished walls, provide spare conduits out of each recessed panelboard to

an accessible location above ceiling. Identify each as SPARE.

- Minimum spare conduits: 5 empty 1 inch (DN27).

- Ground and bond panelboard enclosure according to NEC.

3.2 FIELD QUALITY CONTROL

- Inspect each circuit breaker visually.

- Perform several mechanical ON/OFF operations for each circuit breaker,

- For circuit breakers 6OOA and larger, inspect and test in accordance with NETA STD ATS, except

Section 4.

- For circuit breakers 600A and larger, perforn inspections and tests listed in NETA STD ATS, Section

7.5 for switches, Section 7.6 for circuit breakers.

- For circuit breakers 600A and larger, determine that circuit breaker will trip on over-current condition,

with tripping time to NEMA AB 1 requirements. Include description of testing and results in test report.

END OF SECTION