SECTION 15110 - VALVES

- GENERAL (Not Applicable)

- PRODUCTS

      - GENERAL-DUTY VALVES

        - End Connections:  Threads shall comply with ANSI B1.20.1.  Flanges shall comply with ANSI B16.1 for cast-iron valves and ANSI B16.24 for bronze valves.  Solder-joint connections shall comply with ANSI B16.18.

        - Gate Valves:  Class 125, cast-bronze body and bonnet; with solid disc, copper-silicon alloy stem, brass packing gland, "Teflon" impregnated packing.

        - Ball Valves:  Rated for 150-psig (1035-kPa) saturated steam pressure, 400-psig (2760-kPa) WOG pressure; 2-piece construction; with bronze body, standard (or regular) port, chrome-plated brass ball, replaceable "Teflon" or "TFE" seats and seals, blowout-proof stem, and vinyl-covered steel handle.

        - Plug Valves:  Rated at 150-psig (1035-kPa) WOG; bronze body, with straightaway pattern, square head, and threaded ends.

        - Globe Valves:  Class 125; body and screwed cast-bronze bonnet; with brass or replaceable composition disc, copper-silicon alloy stem, brass packing gland, "Teflon" impregnated packing.

        - Swing Check Valves:  Class 125, cast-bronze body and cap; with horizontal swing, Y-pattern, and bronze disc.

        - Valves for Copper Tube:  Solder ends, except provide threaded ends for heating hot water and low-pressure steam service.

        - Valves for Steel and Plastic Pipe:  Threaded ends.

- EXECUTION

      - INSTALLATION

        - Use gate and ball valves for shutoff duty; globe and ball for throttling duty.

        - Locate valves for easy access and provide separate support where necessary.

        - Install valves for each fixture and item of equipment.

        - Install three-valve bypass around each pressure-reducing valve using throttling-type valves.

        - Install valves in horizontal piping with stem at or above center of pipe.

        - Install valves in a position to allow full stem movement.

        - Install check valves for proper direction of flow in horizontal position with hinge pin level.

END OF SECTION 15110