SECTION 08411 - ALUMINUM-FRAMED STOREFRONTS

- GENERAL

      - SECTION REQUIREMENTS

Show design loads, including wind loads and seismic loads, on Drawings.

        - Structural Performance: Provide systems, including anchorage, capable of withstanding loads indicated.

          - Main-Framing-Member Deflection: Limited to 1/175 of clear span or 3/4 inch (19 mm), whichever is smaller.

          - Structural-Testing: Systems tested according to ASTM E 330 at 150 percent of inward and outward wind-load design pressures do not evidence material failures, structural distress, deflection failures, or permanent deformation of main framing members exceeding 0.2 percent of clear span.

        - Air Infiltration: Limited to 0.06 cfm/sq. ft. (0.3 L/s per sq. m) of system surface area when tested according to ASTM E 283 at a static-air-pressure difference of 6.24 PSF.

        - Water Penetration: Systems do not evidence water leakage when tested according to ASTM E 331 at minimum differential pressure of 20 percent of inward acting wind load design pressure but not less than 8 PSF as defined in AAMA 501 static air pressure differential.

        - Average U-Value: Not more than glass to exterior 0.47, glass to center 0.44, glass to interior 0.41, per AAMA 1503.1.

        - Second Transmission Class (STC) and Outdoor-Indoor Transmission Class (OITC) when tested to AAMA Specification 1801 and in accordance with ASTM E1425 and ASTM E90 the STC and OITC rating shall not be less than

- a.		Glass to Exterior – 38 (STC) and 31 (OITC).

- b.		Glass to Center – 37 (STC) and 30 (OITC).

- c.		Glass to Interior – 38 (STC) and 30 (OITC).

        - Submittals: Product Data, Shop Drawings, and color Samples.

          - For entrance systems, include hardware schedule and locations.

- PRODUCTS

      - ALUMINUM-FRAMED STOREFRONTS

        - Kawneer Trifab VG451, 2x 4½” nominal dimension; non-thermal; front, center, back, multi-plane, structural silicone or weatherseal glazed (Type B) screw spline, shear block, stick, or punched opening fabrication. Or approved equal

        - Aluminum: ASTM B 209 (ASTM B 209M) sheet; ASTM B 221 (ASTM B 221M) extrusions.

        - Glazing: Specified in Division 8 Section "Glazing."

        - Sealants and Joint Fillers: For joints at perimeter of systems as specified in Division 7 Section "Joint Sealants."

        - Doors: 1-3/4-inch- (44.5-mm-) thick glazed doors with minimum 0.125-inch- (3.2-mm-) thick, extruded tubular rail and stile members, mechanically fastened corners with reinforcing brackets that are deep penetration and fillet welded or that incorporate concealed tie-rods, snap-on extruded-aluminum glazing stops, and preformed gaskets.

          - Interior Doors: Provide ANSI/BHMA A156.16 silencers, three on strike jamb of single-door frames and two on head of double-door frames.

          - Exterior Doors: Provide compression weather stripping at fixed stops.  At other locations, provide sliding weather stripping retained in adjustable strip mortised into door edge.

          - Hardware: As specified in Division 8 Section "Door Hardware".

        - Fasteners and Accessories: Compatible with adjacent materials, corrosion-resistant, nonstaining, and nonbleeding.  Use concealed fasteners except for application of door hardware.

        - Fabrication: Fabricate framing in profiles indicated for flush glazing (without projecting stops).  Provide subframes and reinforcing of types indicated or, if not indicated, as required for a complete system.  Factory assemble components to greatest extent possible.  Disassemble components only as necessary for shipment and installation.

          - Door Framing: Reinforce to support imposed loads.  Factory assemble door and frame units and factory install hardware to greatest extent possible.  Reinforce door and frame units for hardware indicated.  Cut, drill, and tap for factory-installed hardware before finishing components.

Class I anodic finishes below are heavier than Class II finishes and are recommend for exterior applications.

        - Aluminum Finish: Comply with NAAMMs "Metal Finishes Manual for Architectural and Metal Products."  Color anodic, Architectural Class I:  AA-M12C22A42/A44.

          - Color: #28 Medium Bronze.

- EXECUTION

      - INSTALLATION

        - Isolate metal surfaces in contact with incompatible metal or corrosive substrates, including wood, by painting contact surfaces with bituminous coating or primer, or by applying sealant or tape recommended by manufacturer.

        - Install components to provide a weatherproof system.

        - Install framing components true in alignment with established lines and grades to the following tolerances:

          - Variation from Plane: Limit to 1/8 inch in 12 feet (3 mm in 3.7 m); 1/4 inch (6 mm) over total length.

          - Alignment: For surfaces abutting in line, limit offset to 1/16 inch (1.5 mm).  For surfaces meeting at corners, limit offset to 1/32 inch (0.8 mm).

          - Diagonal Measurements: Limit difference between diagonal measurements to 1/8 inch (3 mm).

        - Install doors without warp or rack.  Adjust doors and hardware to provide tight fit at contact points and smooth operation.

END OF SECTION 08411