SECTION 16123· LOW-VOLTAGE ELECTRICAL POWER CONDUCTORS AND CABLES

PART1 GENERAL

1.1 SECTION INCLUDES

- Wire and cable for 600 volts and less.

- Wiring connectors and connections.

1.2 REFERENCES

- NECA 1 - Standard for Good Workmanship in Electrical Contracting; National Electrical Contractors

Association; 2006.

- NFPA 70 - National Electrical Code, National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

1.3 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Manufacturer Qualifications: Company specializing in manufacturing the Products specified in this

section with minimum three years documented experience and with service facilities within 100 miles

(160 km) of Project.

- Products: Furnish products listed and classified by Underwriters Laboratories Inc. as suitable for the

purpose specified and indicated.

PART 2 PRODUCTS

2.1 WIRING REQUIREMENTS

- Use only building wire with Type THWN/THHN (dual rated) or XHHW insulation in raceway (ground

wires may be Type TW or THW). Wire shall be color coded per the NEC and as follows:

  - 480Y/277 V, 3 Phase System: Brown, Orange, Yellow with White Neutral and Green Ground.

  - 208Y/120V, 3 Phase System: Black, Red, Blue with White Neutral and Green Ground

  - 120/240V, 1 Phase System: Red and Black with White Neutral and Green Ground.

- Use solid conductor for feeders and branch circuits #8 AWG and smaller. Use stranded conductors

for feeders and branch circuits #6 AWG and larger.

- Use stranded conductors for control circuits.

- Use conductor not smaller than 12 AWG for power and lighting circuits.

- Use conductor not smaller than 16 AWG for control circuits.

- Use #10 AWG conductors for 20 ampere, 120 volt branch circuits longer than 75feet (25 m). This

requirement overrides any circuits shown with #12 AWG wire in panel schedules in the design

drawings. If larger than #10 AWG wire is shown in panel schedules, then conform to panel schedules.

- Conductor sizes are based on copper. Wire shall be copper unless indicated otherwise.

2.2 BUILDING WIRE

- Description: Single conductor insulated wire.

- Conductor: Copper.

- Insulation Voltage Rating: 600 volts.

- Insulation: Thermoplastic material rated 90 degrees C.

PART 3 EXECUTION

3.1 PREPARATION

- Completely and thoroughly swab raceway before installing wire.

3.2 INSTALLATION

- Install wire and cable securely, in a neat and workmanlike manner, as specified in NECA.

- Route wire and cable as required to meet project conditions.

- Wire and cable routing indicated is intended to be diagrammatic.

- Where wire and cable destination is indicated and routing is not shown, determine exact routing and

lengths required.

- Include wire and cable of lengths required to install connected devices within 10ft (3000 mm) of

location shown.

- No wiring shall be installed until the required raceway system, including junction, outlet and device

boxes is completed. Install wiring before painting begins and protect against being painted.

- Branch circuit sizes are noted on the Drawings and must be continuous without reduction in size

throughout their length except where connecting to fixtures or devices.

- Branch circuit wire sizes shall be increased as required where long runs will cause excessive voltage

drop per NEC.

- Wire circuits as described or indicated on the Drawings to achieve a connected load as scheduled.

Should any change be necessary, it must be brought to the GOVERNMENT’S attention.

- Install wire and cable in accordance with the NECA ·Standard of Installation,"

- Use wiring methods indicated.

- Pull all conductors into raceway at same lime.

- Use suitable wire pulling lubricant for building wire 4 AWG and larger.

- Neatly train and lace wiring inside boxes, equipment, and panelboards.

- Clean conductor surfaces before installing lugs and connectors.

- Make splices, taps, and terminations to carry full ampacity of conductors with no perceptible

temperature rise.

- Use split bolt connectors tor copper conductor splices and taps, #4 AWG and larger. Tape

uninsulated conductors and connector with electrical tape to 150 percent of insulation rating of

conductor.

- Use solderless pressure connectors with insulating covers for copper conductor splices and taps, 8

AWG and smaller.

3.3 FIELD QUALITY CONTROL

- Perform field inspection and testing in accordance with Section 01400.

- Test wiring rated 600 volts and less to verify that no short circuits or accidental grounds exist.

Perform insulation resistance tests on wiring No. 4 AWG and larger diameter using an instrument

which applies voltage 01 approximately 500 volts to provide direct reading of resistance. Minimum

resistance shall be 250,000 ohms.

END OF SECTION