SECTION 15080 - MECHANICAL INSULATION

- GENERAL

      - SECTION REQUIREMENTS

        - Submittals:  Product Data for each type of mechanical insulation

        - Quality Assurance:  Labeled with maximum flame-spread rating of 25 and maximum smoke- developed rating of 50 according to ASTM E 84.

- PRODUCTS

      - PIPE INSULATION

        - Preformed Glass-Fiber Pipe Insulation:  ASTM C 547, Class 1, with factory-applied, all-purpose, vapor-retarder jacket.

        - Flexible Elastomeric Cellular Pipe Insulation:  Closed-cell, sponge- or expanded-rubber materials.  Comply with ASTM C 534, Type I.

        - Polyolefin Pipe Insulation:  Unicellular polyethylene, preformed pipe insulation.  Comply with ASTM C 534, Type I, except for density.

      - DUCT AND EQUIPMENT INSULATION

        - Glass-Fiber Board Insulation:  Glass fibers bonded with a thermosetting resin.  Comply with ASTM C 612, Type IB, without facing and with all-service jacket manufactured from kraft paper, reinforcing scrim, aluminum foil, and vinyl film.

        - Glass-Fiber-Blanket Insulation:  Glass fibers bonded with a thermosetting resin;.  Comply with ASTM C 553, Type II, without facing and with all-service jacket manufactured from kraft paper, reinforcing scrim, aluminum foil, and vinyl film.

        - Flexible Elastomeric Cellular Sheet Insulation:  Closed-cell, sponge- or expanded-rubber materials.  Comply with ASTM C 534, Type II.

- EXECUTION

      - INSTALLATION

        - Install vapor barriers on insulated pipes with surface operating temperatures below 60 deg F (15 deg C).

        - Insulate fittings, valves, and specialties.

        - Seal vapor-barrier penetrations for hangers, supports, anchors, and other projections.

        - Coat glass-fiber pipe insulation ends with vapor-barrier coating.

        - Roof Penetrations:  Apply insulation for interior applications to a point even with the top of the roof flashing.

        - Exterior Wall Penetrations:  For penetrations of below-grade exterior walls, terminate insulation flush with mechanical sleeve seal.

        - Interior Walls and Partitions Penetrations:  Apply insulation continuously through walls and partitions, except fire-rated walls and partitions.

        - Fire-Rated Walls and Partitions Penetrations:  Terminate insulation at penetrations through fire-rated walls and partitions.  Seal around penetration with through-penetration firestop systems specified in Division 7.

        - Floor Penetrations:  Terminate insulation at the underside of the floor assembly and at the floor support at top of floor.  Seal around penetration with through-penetration firestop systems specified in Division 7.

        - Glass-Fiber Insulation Installation:  Bond insulation to pipe with adhesive.  Seal seams and joints with vapor-barrier compound.

        - Flexible Elastomeric Insulation Installation:  Seal joints with adhesive.

        - Interior Piping System Applications:  Insulate the following piping systems:

          - Domestic hot water.

          - Refrigerant suction piping.

        - Do not apply insulation to the following systems, materials, and equipment:

          - Flexible connectors.

          - Sanitary drainage and vent piping.

          - Below-grade piping.

          - Chrome-plated pipes and fittings, except for plumbing fixtures for the disabled.

          - Piping specialties, including air chambers, unions, strainers, check valves, plug valves, and flow regulators.

        - Pipe Insulation Thickness Application Schedule:  Insulate piping with the following materials and thicknesses:

          - Domestic Hot Water and Recirculated Hot Water:  1/2-inch (12.7-mm)[preformed glass- fiber or flexible elastomeric pipe insulation.

          - Suction Piping: 3/4-inch (19-mm) flexible elastomeric pipe insulation

        - Install duct insulation as follows:

          - Install insulation continuously on ducts that penetrate walls and floors, except at fire-rated assemblies terminate insulation at the assembly.  Maintain insulation vapor retarder on cold duct.

          - Install removable or segmented insulation on access panel and doors.

          - Install vapor barriers on insulated ducts and plenums with surface operating temperatures below 60 deg F (15 deg C).  Seal joints and seams to maintain vapor barrier on insulation requiring a vapor barrier.

          - Taper glass-fiber insulation ends at a 45-degree angle and seal with adhesive.  Cut ends of flexible elastomeric cellular insulation square and seal with adhesive.

          - Board Insulation Installation:  Secure insulation tight and smooth with speed washers and anchor pins.  Space anchor pins 18 inches (450 mm) apart each way and 3 inches (76 mm) from insulation joints.  Apply vapor-barrier coating compound to insulation in contact, open joints, breaks, punctures, and voids in vapor barrier.

          - Blanket Insulation Installation:  Bond ducts having long sides or diameters smaller than 24 inches (610 mm) with bonding adhesive applied in 6-inch- (150-mm-) wide transverse strips on 12-inch (300-mm) centers.  Bond ducts having long sides or diameters 24 inches (610 mm) and larger with anchor pins spaced 12 inches (300 mm) apart each way.  Apply bonding adhesive to prevent sagging of insulation.  Overlap joints 3 inches (76 mm).  Seal joints, breaks, and punctures with vapor-barrier compound.

        - Duct System Applications:  Insulate indoor concealed supply-, return-, and outside-air ducts.

        - Do not apply insulation to the following systems, materials, and equipment:

          - Fibrous glass ducts.

          - Metal ducts with duct liner.

          - Factory-insulated flexible ducts.

          - Factory-insulated plenums, casings, terminal boxes, and filter boxes and sections.

          - Vibration-control devices.

          - Testing laboratory labels and stamps.

          - Nameplates and data plates.

        - Duct Insulation Thickness and Application Schedule:  Insulate ducts with the following materials and thicknesses:

          - Concealed Applications:  Fiberglass blanket, 1-1/2 inches (38 mm) thick or Fiberglass board, 2 inches (50 mm) thick.

          - Exposed Applications:  Fiberglass board, 2 inches (50 mm) thick.

END OF SECTION 15080