SECTION 16412· ENCLOSED SWITCHES

PART 1 GENERAL

1.1 SECTION INCLUDES

- Fusible switches.

- Non-fusible switches.

1.2 RELATED SECTIONS

- Section 16491 . Fuses.

1.3 REFERENCES

- NECA (INST) NECA Standard of Installation; National Electrical Contractors Association; 1993.

- NEMA FU 1 . Low Voltage Cartridge Fuses; National Electrical Manufacturers Association; 2002

(R2007).

- NEMA KS 1 - Enclosed and Miscellaneous Distribution Equipment Switches (600 Volts Maximum);

National Electrical Manufacturers Association; 2001 (R2006)

.

- NETA STD ATS· Acceptance Testing Specifications for Electrical Power Distribution Equipment and

Systems; International Electrical Testing Association; 2007.

- NFPA 70 . National Electrical Code; National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

1.4 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this

section with minimum three years documented experience and with service facilities within 100 miles

(160 km) of Project.

- Products: Listed and classified by Underwriters Laboratories Inc. as suitable for the purpose specified

and indicated.

PART 2 PRODUCTS

2.1 MANUFACTURERS

- Basis of Design: Square D; www.squared.com.

2.2 COMPONENTS

- Fusible Switch Assemblies: NEMA KS 1, Type HD enclosed load interrupter knife switch

  - Externally operable handle interlocked to prevent opening front cover with switch in ON position.

  - Handle lockable in OFF position.

  - Fuse clips: Designed to accommodate NEMA FU 1, Class R fuses.

- Non-Fusible Switch Assemblies: NEMA KS 1, Type HD enclosed load interrupter knife switch

  - Externally operable handle interlocked to prevent opening front cover with switch in ON position.

  - Handle lockable in OFF position.

- Enclosures: NEMA KS 1

  - Interior Dry Locations: Type 1.

  - Exterior Locations: Type 3R.

PART 3 EXECUTION

3.1 INSTALLATION

- Install in accordance with manufacturer’s instructions.

- Install fuses in fusible disconnect switches.

- Apply adhesive tag on inside door of each fused switch indicating NEMA fuse class and size installed.

3.2 FIELD QUALITY CONTROL

- Visually and mechanically confirm that safety switch is working.

- For switches rated 200A and greater, inspect and test in accordance with NETA STD ATS, except Section 4.

- For switches rated 200A and greater, perform inspections and tests listed in NETA STD ATS, Section 7.5.

END OF SECTION