SECTION 16060 · GROUNDING AND BONDING

PART1 GENERAL

1.1 SECTION INCLUDES

- Grounding and bonding components.

1.2 REFERENCES

- NFPA 70 - National Electrical Code, NFPA (edition adopted by Authority Having Jurisdiction).

1.3 PERFORMANCE REQUIREMENTS

- Grounding System Resistance: 10 ohms.

1.4 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this

section with minimum three years documented experience with service facilities within 100 miles of

Project.

- Products: listed and classified by Underwriters Laboratories Inc. as suitable for the purpose specified

and indicated.

PART 2 PRODUCTS

2.1 CONNECTORS AND ACCESSORIES

- Wire: TW Stranded copper with green coding sized per NEC.

PART 3 EXECUTION

3.1 EXAMINATION

- Verify existing conditions prior to beginning work.

3.2 INSTALLATION

- Provide bonding to meet requirements described in Quality Assurance.

- Bond equipment such as metallic housing and feeder metallic conduits to grounding conductor. Use

grounding bushings, on service conduit and at other points where grounding continuity is broken.

- Provide a bonding jumper for any equipment, motor, fixture or device to which current carrying

conductors are connected that is not bonded directly to the grounded system. Connect bonding

jumper to approved lugs and grounding conduit bushings or clamps.

- Equipment Grounding Conductor: Provide separate, insulated grounding conductor within each

feeder and branch circuit raceway (sized per NEC Section 250). Terminate each end on suitable lug,

bus, or bushing. Metal raceways shall not be used as the sole method of grounding.

3.3 FIELD QUALITY CONTROL

- Test existing grounding system to ensure continuity and that resistance to ground is not excessive

(above 10 ohms). Test each ground rod for resistance to ground before making connections to rod:

tie grounding system together and test for resistance to ground, Make 'resistance measurements in

dry weather, not earlier than 48 hours after rainfall. Notify engineer before proceeding if resistance to

ground is excessive,

END OF SECTION