SECTION 16510 • INTERIOR LUMINAIRES

PARTI GENERAL

1.1 SECTION INCLUDES

- Interior lighting fixtures and accessories.

- Emergency lighting units.

- Exit signs.

- Ballasts.

- Fluorescent lamp emergency power supply

- Lamps.

- Fixture accessories.

1.2  REFERENCES

- ANSI C78.379 . American National Standard for Electric Lamps . Reflector Lamps . Classification of

Beam Patterns: 2006.

- ANSI C82.1 . American National Standard for Lamp Ballast · Line Frequency Fluorescent Lamp

Ballast: 2004.

- ANSI C82.4 • American National Standard for Ballasts for High-Intensity-Discharge and Low Pressure

Sodium Lamps (Multiple-Supply Type): 2002.

- NECA/IESNA 500· Standard for Installing Indoor Commercial Lighting Systems: National Electrical

Contractors Association; 2006.

- NEMA WD 6 . Wiring Devices - Dimensional Requirements; National Electrical Manufacturers

Association: 2002 (R2008).

- NFPA 70· National Electrical Code. National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

- NFPA 101 . Code for Safety to Life from Fire in Buildings and Structures; National Fire Protection

Association (edition adopted by Authority Having Jurisdiction).

1.3 SUBMITIALS

- Product Data (including ballasts and lighting contactors): Provide dimensions, ratings, and

performance data.

1.4 OUALITY ASSURANCE

- Conform to requirements of NFPA 70 and NFPA 101.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this

section with minimum three years documented experience.

- Products: listed and classified by Underwriters Laboratories, Inc. as suitable for the purpose

specified and indicated.

1.5 EXTRA MATERIALS

- Furnish one replacement lamp for each lamp type.

PART 2 PRODUCTS

2.1 GENERAL REQUIREMENTS FOR INTERIOR LIGHTING FIXTURES

- Provide products that comply with requirements of NFPA 70 and NFPA 101.

- Provide products listed and classified by Underwriters Laboratories Inc. as suitable for the purpose

specified and indicated.

- Provide accessories and fittings as recommended by manufacturer to properly and completely install

and wire fixtures.

- Electrical Characteristics: 120/277 volts. 60 Hz, unless otherwise indicated.

2.2 LUMINAIRES

- Furnish products as indicated in Schedule included on the Drawings. Confirm that the fixtures

scheduled are the correct, voltage, wattage, size and mounting type and are listed for location used

(i.e. damp or wet locations) before ordering fixtures, ballasts, and lamps. For substitutions, see

section 16050.

- Although not specifically shown or specified, all light fixtures shall be provided with all necessary

optional accessories and mounting hardware for installation as indicated or required.

- Provide insulated ceiling (IC) rated fixtures where recessed incandescent, compact fluorescent, or

low voltage light fixtures come into direct contact with insulation.

2.3 BALLASTS AND CONTROL UNITS

- Fluorescent Ballasts:

  - Ballasts for fluorescent fixtures shall be as noted on Fixture Schedule. Energy efficient type

ballasts shall be specifically approved for operation with the specified lamps. Electronic ballasts

shall have low total harmonic distortion (less than or equal to 20 percent) to avoid excessive

harmonics and overloading of neutrals. All ballasts shall have an A noise rating. Provide rapid

start ballasts for all fluorescent fixtures controlled by occupancy sensors.

  - Voltage: Match luminaire voltage.

- High Intensity Discharge (HID) Ballasts: ANSI C82.4, metal halide lamp ballast, suitable for lamp

specified.

  - Ballast for HID fixtures shall be high power factor type selected for type and wattage of lamp

supplied. All ballasts shall have an A noise rating.

  - Voltage: Match luminaire voltage.

- Fluorescent Lamp Emergency Power Supply: Emergency battery power supply suitable for

installation in ballast compartment of fluorescent fixture.

  - Lamp Ratings: one T5, T5HO, or T8 lamp providing 1100 lumens minimum. For compact

fluorescent fixtures, provide 600 lumens minimum, per fixture.

  - Battery: Sealed lead calcium type. rated for 10 year life.

  - Include TEST switch and AC ON indicator light, installed tp be operable and visible from the

outside of an assembled fixture.

2.4 LAMPS

- Lamp Types: As specified for each fixture.

- Reflector Lamps: Beam patterns in accordance with ANSI C78.379.

PART3 EXECUTION

3.1 INSTALLATION

- Install fixtures securely, in a neat and workmanlike manner, as specified in NECA 500 (commercial

lighting).

- Install suspended luminaires and exit signs using pendants supported from swivel hangers. Provide

pendant length required to suspend luminaire at indicated height.

- Support luminaires larger than 2 x 4 foot (600 x 1200 mm) size independent of ceiling framing.

- Locate recessed ceiling luminaires as indicated on reflected ceiling plan.

- Install surface mounted luminaires and exit signs plumb and adjust to align with building lines and

with each other. Secure to prevent movement.

- Support fixtures (2 x 4 foot and smaller) to be recessed in readily removable tile ceilings (lay-in type)

from the T-bar tile support and connect to remote mounted 4" square (minimum size, conform to

NEC) junction boxes with approved six foot long (four feet long for plenum ceilings), 3/8" flexible

conduit "fixture whip' with grounding conductor bonded between conduit system and fixture.

- Connect single-connected fixtures, surface or stem hung, with heat resistant fixture wire. Connect

multiple-connected fluorescent fixtures, surface or stem hung, with type THHN heat resistant

thermoplastic wire of a size indicated for branch circuit.

- Install clips to secure recessed grid-supported luminaires in place.

- Provide sloped ceiling adaptors and all other required hardware as necessary to properly install

ceiling mounted light fixtures in sloped ceilings.

- Install wall mounted luminaires, emergency lighting units, and exit signs at height as indicated on

drawings.

- Install accessories furnished with each fixture.

- Make wiring connections to branch circuit using building wire with insulation suitable for temperature

conditions within fixture; use flexible conduit.

- Connect luminaires and exit signs to branch circuit outlets provided under Section 16138 using

flexible conduit.

- Make wiring connections to branch circuit using building wire with insulation suitable for temperature

conditions within luminaire.

- Bond products and metal accessories to branch circuit equipment grounding conductor.

- Install specified lamps in each emergency lighting unit, exit sign, and luminaire.

3.2 FIELD QUALITY CONTROL

- Operate each fixture after installation and connection. Inspect for proper connection and operation.

3.3 ADJUSTING

- Aim and adjust fixtures as indicated.

- Position exit sign directional arrows as indicated.

3.4 CLEANING

- Clean electrical parts to remove conductive and deleterious materials.

- Remove dirt and debris from enclosures.

- Clean photometric control surfaces as recommended by manufacturer.

- Clean finishes and touch up damage. Also remove all instruction tags.

3.5 CLOSEOUT ACTIVITIES

- Demonstrate fixture operation for minimum of two hours.

3.6 PROTECTION

- Re-lamp luminaires that have failed lamps at Substantial Completion.

3.7 SCHEDULE· See Drawings

END OF SECTION