SECTION 16271 - PAD-MOUNTED TRANSFORMER

PART 1 GENERAL

1.1 This specification covers the electrical and mechanical characteristics of 45-3750 kVA Three-Phase Step-Down

Pad-Mounted Distribution Transformers with secondary voltages not exceeding 700V. Transformers shall

be Cooper Power Systems or approved equal.

1.2 All characteristics, definitions, and terminology, except as specifically covered in this specification, shall be

in accordance with the latest revision of the following ANSI and NEMA standards.

C57.12.00 · IEEE Standard General Requirements for Liquid-Immersed Distribution, Power, and Regulating Transformers.

C57.12.26· IEEE Standard for Pad-Mounted, Compartmental-Type, Self-Cooled, Three-Phase Distribution Transformers for Use with Separable Insulated High-Voltage Connectors (34500GrdY/19920

Volts and Below; 2500 kVA and Smaller).

C57_12.28 - Pad-Mounted Equipment - Enclosure Integrity.

C57.12.34· IEEE Standard Requirements for Pad-Mounted, Compartmental-Type, Self-Cooled,

Three-Phase Distribution Transformers (2500 kVA and Smaller) - High Voltage: 34500GrdY/19920 Volts

and Below; low-Voltage: 480 Vo1t 2500 kVA and Smaller. (issued in March 2005 - combines C57.12.22

and C57.12.26)

C57.12.90 - IEEE Standard Test Code for liquid-Immersed Distribution, Power, and Regulating Transformers and IEEE Guide for Short-Circuit Testing of Distribution and Power Transformers.

C57.91 - Guide for Loading Mineral-Oil-Immersed Transformers.

PART 2 PRODUCTS

2.1 APPROVED MANUFACTURERS

Cooper Power Systems-Waukesha WI, or approved equal

2.2 RATINGS

The transformer shall be designed in accordance with this specification and the kVA rating shall be as shown on the drawings. The primary voltage, and the basic lightning impulse insulation level (BIL) shall be 22,860gy, 125 kVBIL

The KVA rating, secondary voltage, configuration, and the basic insulation level (BIL) of the secondary voltage shall be as shown on the drawings.

The transformer shall be furnished with full capacity high-voltage taps. The taps shall be +/- 2 - 2 1/2% above and below nominal voltage. The tap changer shall be clear1y labeled to reflect that the transformer must be de-energized before operating the tap changer as required in Section 3.3 of ANSI C57.12.26. Taps shall be provided on the higher voltage of dual voltage primary units. The tap changer switch shall be an externally operated. snap action switch with a hotstick-operable handle.

The average winding temperature rise above ambient temperature, when tested at the transformer rating shall not exceed 65 deg C.

The percent impedance, secondary voltage, as measured on the rated voltage connection, shall be per the drawings.

2.3 HIGH VOLTAGE COMPARTMENT

High-voltage compartment shall contain the incoming line, insulated high-voltage load-break connectors, bushing well inserts, six high-voltage bushing wells configured for loop feed application, load-break switch handle(s), access to oil immersed fuses dead-front surge arresters, tap changer handle, connector parking stands and ground pad.

Bushing Style:

The high voltage bushings shall be 25 kV 200A bushing wells with inserts. The bushings shall be externally removable and have removable stud. The HV terminations shall be manufactured by the transformer manufacturer.

Bushing Configuration:

The transformer shall be provided with six (6) high voltage bushings in accordance of ANSI C57.12.34 for loop feed configurations. The bushing heights shall be in accordance with of ANSI C57.12.34.

2.4 SECONDARY VOLTAGE COMPARTMENT

Secondary voltage compartment shall contain low-voltage bushings with NEMA spade terminals, accessories, metering, stainless steel or laser-etched anodized aluminum diagrammatic transformer nameplate, and ground pad.

Bushing Style:

The transformer shall be provided with tin-plated spade-type bushings. The spacing of the connection holes shall be 1.75" on center, per ANSI C57.12.34 figure 13.

Bushing supports shall be provided for units requiring 10 or more connection holes. Bushing supports shall be attached to the cabinet sidewalls; tank-mounted support mountings are not acceptable.

Bushing Configuration:

The transformer shall be provided with bushings in a staggered arrangement in accordance with of ANSI C57.12.34.

2.5 TRANSFORMER PROTECTION AND SWITCHING

Over-current Protection:

The high-voltage over-current protection scheme provided with the transformer shall be an externally removable load-break expulsion Bay-O-Net fuse assembly with a flapper valve to minimize oil spillage. The bayonet fuses shall be in series with ELSP under-oil partial-range current-limiting back-up fuses with an interrupting rating of 50,000 A

Overvoltage Protection:

The high-voltage overvoltage protection scheme provided with the transformer shall protect the high voltage winding.

15.3KV MCOV Distribution Class M.O.V.E. Deadfront elbow arresters shall be supplied.

2.6 GENERAL DESIGN

Core and coil

The core and coil shall be vacuum processed to ensure maximum penetration of insulating fluid into the coil insulation system. While under vacuum, the windings will be energized to heat the coils and drive out moisture, and the transformer will be filled with preheated filtered degassed insulating fluid. The core shall be manufactured from burr-free, grain-oriented silicon steel and shall be precisely stacked to eliminate gaps in the corner joints. The coil shall be insulated with B-stage, epoxy coated, diamond pattern, insulating paper, which shall be thermally cured under pressure to ensure proper bonding of conductor and paper.

Dielectric fluid

The dielectric coolant shall be listed less-flammable fluid meeting the requirements of National Electrical Code Section 450-23 and the requirements of the National Electrical Safety Code (IEEE C2-2002), Section 15. The dielectric coolant shall be non-toxic , non-bio accumulating and be readily and completely biodegradable per EPA OPPTS 835.3100. The base fluid shall be 100% derived from edible seed oils and food grade performance enhancing additives. The fluid shall not require genetically altered seeds for its base oil. The fluid shall result in zero mortality when tested on trout fry (per OECO G.L. 203).  The fluid shall be certified to comply with the US EPA Environmental Technology Verification (ETV) requirements, and tested for compatibility with transformer components. The fluid shall be Factory Mutual Approved, UL Classified Dielectric Medium (UL-EOUV) and UL Classified Transformer Fluid (UL-EOVK), Envirotemp FR3TM fluid.

Tank and Cabinet Enclosure

The high-voltage and low-voltage compartments, separated by a metal barrier, shall be located side-by-side on one side of the transformer tank. When viewed from the front, the low-voltage compartment shall be on the right. Each compartment shall have a door that is constructed so as to provide access to the high voltage compartment only after the door to the low-voltage compartment has been opened. There shall be one or more additional fastening devices that must be removed before the high-voltage door can be opened. Where the low-voltage compartment door is of a flat panel design, the compartment door shall have three-point latching with a handle provided for a locking device. Hinge pins and associated barrels shall be constructed of corrosion-resistant material, passivated AISI Type 304 or the equivalent.

A recessed, captive, penta-head bolt that meets the dimensions per ANSI C57.12.28 shall secure all access doors.

The enclosure integrity of the tank and cabinet shall meet the requirements for tamper resistance set forth in ANSI C57.12.28 including but not limited to the pry test, pull test, and wire probe test.

The compartment depth shall be in accordance with C57.12.34, unless additional depth is specified.

The tank base must be designed to allow skidding or rolling in any direction. Lifting provisions shall consist of four lifting lugs welded to the tank.

The tank shall be constructed to withstand 7 psi without permanent deformation, and 15 psi without rupture. The tank shall include a 15 psig pressure relief valve with a minimum flow rate of 35 SCFM.

The tank and cabinet coating shall meet all the requirements of ANSI C57.12.28 including:

Sail Spray Test

Crosshatch Adhesion Test

Humidity Test

Impact Test

Oil Resistance Test

Ultraviolet Accelerated Weathering Test

Abrasion Resistance - Taber Abraser

The exterior of the unit shall be painted Munsell 7GY3.29/1.5 green, in color (confirm color with Government). The cabinet interior and tank face shall be painted gray for ease of viewing the inside the compartment.

The tank shall be complete with an anodized aluminum laser engraved nameplate. This nameplate shall meet Nameplate B per ANSI C57.12.00.

2.7 ACCESSORIES

The following accessories shall be provided :

Bolted main tank cover (1000 kVA and below)

Welded Main Tank Cover with bolted handhole (1500 kVA and above)

1.0” upper fill plug

1.0” drain plug in LV compartment (45-500 kVA)

1.0” drain valve w/sampling device in LV compartment (750-3750 kVA)

Automatic pressure relief valve

Metal drip shield with bayonets

20” deep cabinet

Ground provisions per C57.12.34 section 9.11.

Meet NEMA TR-l sound levels

Liquid level gauge

Dial-type thermometer gauge

Pressure vacuum gauge

Spare bayonet fusing

304 stainless steel tank base and cabinet.

PART 3 EXECUTION

3.1 SHIPPING

Units 1000 kVA and below shall be palletized. Units 1500 kVA and larger shall be loaded and unloaded with overhead cranes.

3.2 TESTING & TOLERANCES

All units shall be tested for the following:

No-load losses at rated current

Total (85°C) losses at rated current

Percent Impedance (85°C) at rated current

Excitation current (100% voltage) test

Winding resistance measurement tests

Ratio tests using all tap settings

Polarity and phase relation tests

Induced potential tests

Full wave and reduced wave impulse test

In addition, the manufacturer shall provide certification upon request for all design and other tests listed in

C57.12.00, including verification that the design has passed short circuit criteria per ANSI C57.12.00 and

C57.12.90.

3.3 DATA WITH PROPOSAL

The following data shall be submitted with the proposal:

Percent Impedance

Typical record drawings

Approval drawings (furnished at time of order)

END OF SECTION