SECTION 16155 - EQUIPMENT WIRING

PART1 GENERAL

1.1 SECTION INCLUDES

- Electrical connections to equipment.

1.2 REFERENCES

- NEMA WD 1 • General Color Requirements for Wiring Devices; National Electrical Manufacturers

Association; 1999 (R 2005).

- NEMA WD 6 • Wiring Devices · Dimensional Requirements; National Electrical Manufacturers

Association; 2002 (R2oo8).

- NFPA 70 . National Electrical Code, National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

1.3 OUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Products: Listed and classified by Underwriters laboratories Inc. as suitable for the purpose specified

and indicated.

1.4 COORDINATION

- Obtain and review shop drawings, product data, manufacturer's wiring diagrams, and manufacturer's

instructions for equipment furnished under other sections.

- Determine connection locations and requirements.

- Sequence rough-in of electrical connections to coordinate with installation of equipment.

- Sequence electrical connections to coordinate with start-up of equipment.

PART 2 PRODUCTS

2.1 MATERIALS

- Disconnect Switches: As follows and in individual equipment sections:

  - Safety switches shall be quick-make, quick-break, heavy duty type in sheet steel enclosure,

except as required for rain tight installations, with door cover interlock. Provide fused type safety

switches and fuses where indicated on the Drawings or as required by Code. Fused switches

shall utilize Class A fuseholders and fuses, unless indicated otherwise.

- Wiring Devices: As specified in Section 16140.

- Flexible Conduit: As specified in Section 16131 .

- Wire and Cable: As specified in Section 16123.

- Boxes: As specified in Section 16138.

PART 3 EXECUTION

3.1 EXAMINATION

- Verify that equipment is ready for electrical connection, wiring, and energization.

3.2 ELECTRICAL CONNECTIONS

- Make electrical connections in accordance with equipment manufacturer's instructions.

- Make all final power feed connections to starters and/or motorized equipment installed by Heating

and Air Conditioning and Plumbing Contractors as indicated or required. Refer to Electrical Sections

of other Contractors' Specifications for further information.

- For air handling equipment with separate "field· installed" heater unit, provide fuse block with fuses,

wiring and power connections for fan motor tapped to unit disconnect switch.

- Verify all equipment for service and characteristics provided prior to rough-in and connection.

Provide a grounding conductor for all equipment connected with flexible conduit and bond to conduit

system and metallic frame of equipment.

- Be responsible for securing and installing proper insulated conductors required for equipment of

higher temperature range beyond that of specified branch circuit type.

- Make conduit connections to equipment using flexible metal conduit. Use liquid-tight flexible metal

conduit with water1ight connectors in damp or wet locations and for all motors and vibrating

equipment.

- Connect heat producing equipment using wire and cable with insulation suitable for temperatures

encountered.

- Provide receptacle outlet to accommodate connection with attachment plug.

- Provide cord and cap where field-supplied attachment plug is required.

- Install suitable strain-relief clamps and fittings for cord connections at outlet boxes and equipment

connection boxes.

- Install disconnect switches, controllers, control stations, and control devices to complete equipment

wiring requirements.

- Install terminal block jumpers to complete equipment wiring requirements.

- Install interconnecting conduit and wiring between devices and equipment to complete equipment

wiring requirements.

END OF SECTION