SECTION 15055 - COMMON PIPING REQUIREMENTS

- GENERAL (Not Applicable)

- PRODUCTS

      - SUPPORTING DEVICES

        - Hanger and Pipe Attachments:  Factory fabricated with galvanized coatings; nonmetallic coated for hangers in direct contact with copper tubing.

        - Building Attachments:  Powder-actuated-type, drive-pin attachments with pullout and shear capacities appropriate for supported loads and building materials; UL listing and FM approval for fire-protection systems.

        - Mechanical-Anchor Fasteners:  Insert-type attachments with pullout and shear capacities appropriate for supported loads and building materials; UL listing and FM approval for fire-protection systems.

- EXECUTION

      - INSTALLATION

        - Install piping free of sags and bends.

        - Install fittings for changes in direction and branch connections.

        - Install sleeves for pipes passing through concrete and masonry walls, and concrete floor and roof slabs.

        - Exterior Wall, Pipe Penetrations:  Mechanical sleeve seals installed in steel or cast-iron pipes for wall sleeves.

        - Fire-Barrier Penetrations:  Seal pipe penetrations with through-penetration firestop systems specified in Division 7.

        - Install unions adjacent to each valve and at final connection to each piece of equipment.

        - Install dielectric unions and flanges to connect piping materials of dissimilar metals in gas, compressed air, and vacuum piping.

        - Install dielectric coupling and nipple fittings to connect piping materials of dissimilar metals in water and steam piping.

      - HANGERS AND SUPPORTS

        - Install building attachments within concrete or to structural steel.  Install additional attachments at concentrated loads, including valves, flanges, guides, strainers, expansion joints, and at changes in direction of piping.

        - Install powder-actuated drive-pin fasteners in concrete after concrete is cured.  Do not use in lightweight concrete or in slabs less than 4 inches (100 mm) thick.

        - Install mechanical-anchor fasteners in concrete after concrete is cured.  Do not use in lightweight concrete or in slabs less than 4 inches (100 mm) thick.

        - Load Distribution:  Install hangers and supports so piping live and dead loading and stresses from movement will not be transmitted to connected equipment.

END OF SECTION 15055