# SECTION 15835

# FANS

- PART 1 – GENERAL

  - DESCRIPTION

    - This section applies to all fans shown on the Drawings and specified in other sections.

  - SUBMITTALS

    - Submit product data and complete performance data to include noise levels.

    - Submit performance curves for fans of 1/2 horsepower or greater.

    - Submit tabular performance data for fans less than 1/2 horsepower.

    - Installation details for exterior and roof-mounted fans and/or curbs, which meet the Building Code wind load requirements.

- PART 2 – PRODUCTS

- 2.01	GENERAL

- A.	Fan data shall be AMCA rated, tested and certified for air and sound performance.  All fans shall be UL approved.

    - Fans shall be selected to operate in the stable region of their characteristic performance curve.

    - Equipment submitted shall be equal in all respects and provide the materials of construction and all standard features; scheduled or specified options or accessories of the equipment specified and scheduled on the drawings.

    - All fan wheels shall be statically and dynamically balanced.  Fan operation shall be free of undo noise and vibration at design conditions and throughout the fans normal selection range.

    - Fan drives shall be direct or belt type as scheduled.  Belt drives shall be adjustable and sized to transmit 150 percent of motor horsepower.

    - Motors shall be provided with electrical characteristics scheduled on the Drawings.  All motors shall meet the requirements of Division 16 and shall provide overload protection and a minimum service factor of 1.15.

    - Furnish fan accessories as scheduled on the Drawings to include disconnects, roof curbs, dampers, caps, and special finishes.

- 2.01	CABINET CENTRIFUGAL FANS

- A.	Fan shall be fully enclosed, forward curved centrifugal type of galvanized steel construction.

- B.	Performance and drives shall be as scheduled on the Drawings.

- C.	Fan shall be rigidly constructed to resist torsional stresses; free from objectionable vibration or noise; statically and dynamically balanced and capable of operating at speed not less that 1-1/2 times the required operating speed.

- D.	Housing shall be constructed of heavy gage galvanized steel with one inch thick fiberglass lining meeting NFPA 90 A requirements.  The housing shall be capable of modification for bottom inlet on in-line application.

- E.	Fan discharge opening shall be provided with a backdraft damper unless indicated otherwise on the Drawings.

- F.	Cabinet inlet shall be provided with a one-piece plastic or aluminum grille with enamel finish and sight proof appearance.

- G.	Provide non-fused disconnect switch complete with factory wiring and mounting.

    - Where scheduled provide wall or roof jacks constructed of .063 inch aluminum with continuous welded watertight seams. Roof jack shall be of the roofed-over flashing type.  Wall jacks shall have a flanged frame.  Provide jacks with bird screens.

    - Provide a variable speed controller with dial and cover plate where scheduled on the Drawings.

- PART 3 - EXECUTION

- 3.01	INSTALLATION

- A.	Install fans where indicated in accordance with the manufacturer's instructions and the Drawings.

    - Provide vibration isolation where indicated on the Drawings or specified in other sections of the Specifications.

- 3.02	START UP

- A.	Verify proper electrical connection to the fan motor and assure proper fan wheel rotation upon start up.

- B.	Assure fan bearings are properly lubricated before start up.

    - Check fan for undo vibration or noise during operation.

    - Adjust fan speed at drive or speed controller to achieve specified performance.

# END OF SECTION