SECTION 02553 - NATURAL GAS DISTRIBUTION

- GENERAL

      - SECTION REQUIREMENTS

        - Summary:  This Section includes gas piping outside the building.  Service meter assembly is provided by the gas utility.

        - Unless otherwise indicated, the minimum pressure requirements for natural gas distribution system piping is 100 psig (690 kPa) for piping, valves, and service regulators.

        - Comply with NFPA 54, "National Fuel Gas Code."

        - Comply with NFPA 70, "National Electrical Code."

- PRODUCTS

      - PIPE AND FITTINGS

        - Steel Pipe:  ASTM A 53, Type E or S, Grade B; Schedule 40, black.

        - Malleable-Iron Fittings:  ASME B16.3, Class 150, standard pattern, with threads complying with ASME B1.20.1.

        - Unions:  ASME B16.39, Class 150, black malleable iron; female pattern; brass-to-iron seat; ground joint.

        - PE Pipe:  ASTM D 2513, SDR 11.

        - PE Fittings:  ASTM D 2683, socket type or ASTM D 3261, butt type with dimensions matching ASTM D 2513, SDR 11, PE pipe.

        - Transition Fittings:  Type, material, and with end connections matching piping being joined.

      - VALVES

Paragraph below is suitable for valves 2-inch NPS (DN50) and smaller.

        - Bronze Gas Valves:  ASME B16.33, MSS SP-78, UL 842, or AGA/IAS listing; 100-psig (690-kPa) WOG, bronze body, bronze plug, straightaway pattern, square head, tapered-plug type, and threaded ends.  Include locking device.

        - Plastic Valves:  PE made for gas distribution, with nut or flat head for key operation, and complying with ASME B16.40, UL 842, or AGA/IAS listing.

        - Valve Boxes:  Cast-iron two-section box.  Top section includes cover with "GAS" lettering.  Bottom section includes base of size to fit over valve and barrel about 5 inches (125 mm) in diameter.

        - Earthquake, Automatic Shutoff Valves:  ANSI Z21.70, mechanical operation, with threaded ends.

      - SPECIALTIES

        - Service Line Risers:  PE pipe with coated, annodeless, steel pipe casing on riser section.  Include inlet for heat-fusion connection to PE pipe and outlet for connection to shutoff valve.

        - Strainers:  Y-pattern, full size of connecting piping.  Include Type 304 stainless-steel screens with 3/64-inch (1.2-mm) perforations, unless otherwise indicated.

        - Metallic-Lined Plastic Underground Warning Tapes:  Polyethylene plastic tape with metallic core, 6 inches (150 mm) wide by 4 mils (0.1 mm) thick, solid yellow color with continuously printed caption in black letters "CAUTION--GAS LINE BURIED BELOW."

- EXECUTION

      - INSTALLATION

        - Comply with NFPA 54, "Prevention of Accidental Ignition."

        - Install buried gas distribution system piping with a 3-foot (900-mm) minimum cover.  Include underground warning tape.

        - Install drips at points where condensate may collect, including gas meter outlets.  Locate where readily accessible to permit cleaning and emptying.  Do not install where condensate would be subject to freezing.

        - Install strainers on inset side of service regulators and earthquake valves.

        - Terminate vent piping with turned-down reducing-elbow fittings with corrosion-resistant insect screens in large end.

        - Install containment conduits for buried gas piping where indicated.  Vent conduits to atmosphere.  Terminate vents with turned-down reducing-elbow fittings with corrosion-resistant insect screens in large ends.

        - Install underground, plastic, gas distribution piping according to ASTM D 2774.

        - Install plastic shutoff valves on branch connections to existing underground gas distribution piping.  Install valves with valve boxes.

        - Install metal shutoff valves on aboveground, gas distribution piping.

        - Install aboveground, metal shutoff valves in accessible locations, protected from physical damage.  Include metal tag indicating piping systems supplied, attached to valve with metal chain.

        - Install aboveground, natural gas distribution piping upstream from equipment shutoff valves, electrically continuous, and bonded to grounding electrode according to NFPA 70.

        - Do not use gas piping as a grounding electrode.

        - Install continuous, plastic, underground warning tape during backfilling of trench for underground gas piping.  Locate 6 to 8 inches (150 to 200 mm) below finished grade, directly over piping.

END OF SECTION 02553