SECTION 16302 - MEDIUM VOLTAGE UNDERGROUND ELECTRICAL DISTRIBUTION

PART 1 . GENERAL

1.1 REFERENCES

The publications listed below form a part of this specification to the extent referenced. The publications are referred

to within the text by the basic designation only.

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE)

IEEE C2 	(2007) National Electrical Safety Code

INSULATED CABLE ENGINEERS ASSOCIATION (ICEA)

ICEA S-94-649	(2004) Standard for Concentric Neutral Cable Rated 5 Through 46 KV

INTERNATIONAL ELECTRICAL TESTING ASSOCIATION (NETA)

NETA ATS	(1999) Acceptance Testing Specifications

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA TC2	(2003) Electrical Polyvinyl Chloride (PVC) Tubing and Conduit

NEMA WC 74 	(2000) 5-46 kV Shielded Power Cable for Use in the Transmission and Distribution of Electric Energy

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70	National Electrical Code (edition adopted by AHJ)

UNDERWRITERS LABORATORIES (UL)

UL 1072 	(2006) Medium-Voltage Power Cables

UL 467 		(2004) Grounding and Bonding Equipment

1.2 DEFINITIONS

- Unless otherwise specified or indicated, electrical and electronics terms used in these

specifications, and on the drawings, shall be as defined in IEEE STD 100.

- In the text of this section, the words conduit and duct are used interchangeably and have the same

meaning.

- In the text of this section, "medium voltage cable splices”, and "medium voltage cable joints” are used interchangeably and have the same meaning.

1.3 SUBMITIALS

The following shall be submitted in accordance with SUBMITTAL PROCEDURES:

SD-03 Product Data

Medium voltage cable

SD-06 Test Reports

Arc-proofing test for cable fireproofing materials

Medium voltage cable qualification and production tests

Field Acceptance Checks and Tests

Arc-proofing test for cable fireproofing tape

Cable Installation Plan and Procedure

SD-07 Certificates

Cable splicer/terminator

Cable Installer Qualifications

1.4 QUALITY ASSURANCE

1.4.2 Certificate of Competency for Cable Splicer/Terminator

Certification of the qualification of the cable splicer/terminator shall be submitted, for approval, 30 days

before splices or terminations are to be made in medium voltage (5 kV to 35 kV) cables. The certification

shall include the training, and experience of the individual on the specific type and classification of cable to

be provided under this contract. The certification shall indicate that the individual has had three or more

years recent experience splicing and terminating medium voltage cables. The certification shall also list a

minimum of three splices/terminations that have been in operation for more than one year. In addition, the

individual may be required to perform a dummy or practice splice/termination in the presence of the

Contracting Officer, before being approved as a qualified cable splicer. If that additional requirement is

imposed, the Contractor shall provide short sections of the approved types of cables along with the

approved type of splice/termination kit, and detailed manufacturer's instructions for the cable to be spliced.

The Contracting Officer reserves the right to require additional proof of competency or to reject the individual

and call for certification of an alternate cable splicer.

1.4.3 Cable Installer Qualifications

Provide at least one on site person in a supervisory position with a documentable level of competency and

experience to supervise all cable pulling operations. Provide a resume showing the cable installers'

experience in the last three years, including a list of references complete with points of contact, addresses

and telephone numbers.

1.4.4 Regulatory Requirements

In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though

the word, "shall" had been substituted for "should" wherever it appears. Interpret references in these

publications to the "authority having jurisdiction," or words of similar meaning, to mean the Contracting

Officer. Equipment, materials, installation, and workmanship shall be in accordance with the mandatory and

advisory provisions of NFPA 70 unless more stringent requirements are specified or indicated.

1.4.5 Standard Products

Provide materials and equipment that are products of manufacturers regularly engaged in the production of

such products which are of equal material, design and workmanship. Products shall have been in

satisfactory commercial or industrial use for 2 years prior to bid opening. The 2-year period shall include

applications of equipment and materials under similar circumstances and of similar size. The product shall

have been on sale on the commercial market through advertisements, manufacturers' catalogs, or

brochures during the 2-year period. Where two or more items of the same class of equipment are required,

these items shall be products of a single manufacturer; however, the component parts of the item need not

be the products of the same manufacturer unless stated in this section.

1.4.5.1 Alternative Qualifications

Products having less than a 2·year field service record will be acceptable if a certified record of

satisfactory field operation for not less than 6000 hours, exclusive of the manufacturers' factory or

laboratory test is furnished.

1.4.5.2 Material and Equipment Manufacturing Date

Products manufactured more than 3 years prior to date of delivery to site shall not be used, unless

specified otherwise,

PART 2 . PRODUCTS

2.1 MEDIUM VOLTAGE CABLE

Cable (conductor) sizes are designated by American Wire Gauge (AWG) and Thousand Circular Mils (Kcmil).

Conductor and conduit sizes indicated are for copper conductors unless otherwise noted. Insulated conductors shall

have the date of manufacture and other identification imprinted on the outer surface of each cable at regular intervals

throughout cable length. Wires and cables manufactured more than 24 months prior to date of delivery to the site

shall not be accepted. Provide single conductor type cables unless otherwise indicated.

2.1.1 Cable Configuration

Provide concentric neutral underground distribution cable conforming to ICEA 5-94-649. Provide cables

manufactured for use in duct. Cable shall be rated 25 kV with 133 percent insulation level.

2.1.2 Conductor Material

Provide concentric-lay-stranded, aluminum conductors.

2.1.3 Insulation

Provide cross-linked thermosetting polyethylene (XLPE) insulation conforming to the requirements of NEMA

WC 74 and ICEA S-94·649.

2.1.4 Neutrals

Concentric neutrals conductors shall be aluminum, having a combined ampacity 1/3 of the phase conductor

ampacity rating.

2.1.5 Jackets

Cables shall be provided with a PVC jacket. Direct buried cables shall be rated for direct burial. Provide type

UD cables with an overall jacket. Provide PVC jackets with a separator that prevents contact when

underlying semiconducting insulating shield.

PART 3 - EXECUTION

3.1 INSTALLATION

Install equipment and devices in accordance with the manufacturer's published instructions and with the

requirements and recommendations of NFPA 70 and IEEE as applicable.

3.2 CABLE INSPECTION

Prior to installation, each cable reel shall be inspected for correct storage positions, signs of physical damage, and

broken end seals. If end seal is broken, moisture shall be removed from cable prior to installation in accordance with the cable manufacturer's recommendations.

3.3 CABLE INSTALLATION PLAN AND PROCEDURE

The Contractor shall obtain from the manufacturer an installation manual or set of instructions which addresses such

aspects as cable construction, insulation type, cable diameter, bending radius, cable temperature limits for

installation, lubricants, coefficient of friction, conduit cleaning, storage procedures, moisture seals, testing for and

purging moisture, maximum allowable pulling tension, and maximum allowable sidewall bearing pressure. The

Contractor shall then prepare a checklist of significant requirements and perform pulling calculations and prepare a

pulling plan which shall be submitted along with the manufacturers instructions in accordance with submittals. Cable shall be installed strictly in accordance with the cable manufacturer's recommendations.

3.4 CABLE PULLING

Test existing duct lines with a mandrel and thoroughly swab out to remove foreign material before pulling cables.

Pull cables down grade with the feed-in point at the manhole or buildings of the highest elevation. Use flexible cable feeds to convey cables through manhole opening and into duct runs. Do not exceed the specified cable bending radii when installing cable under any conditions, including turn-ups into switches, transformers, switchgear, switchboards, and other enclosures. If basket-grip type cable-pulling devices are used to pull cable in place, cut off the section of cable under the grip before splicing and terminating.

3.4.1 Cable lubricants

Use lubricants that are specifically recommended by the cable manufacturer for assisting in pulling jacketed

cables.

3.5 GROUNDING SYSTEMS

Provide grounding system as indicated, in accordance with NFPA 70 and IEEE C2, and as specified herein.

Noncurrent-carrying metallic parts associated with electrical equipment shall have a maximum resistance to solid

earth ground not exceeding the following values:

Pad·mounted transformers without		5 ohms

protective fences

Ground in manholes			5 ohms

Grounding other metal enclosures of	5 ohms

primary voltage electrical and

electrically-operated equipment

3.5.1 Grounding Electrodes

Provide cone pointed driven ground rods driven full depth plus [150 mm] 6 inches, installed to provide an

earth ground of the appropriate value for the particular equipment being grounded. If the specified ground

resistance is not met, an additional ground rod shall be provided in accordance with the requirements of

NFPA 70 (placed not less than 6 feel from the first rod). Should the resultant (combined) resistance exceed

the specified resistance, measured not less than 48 hours after rainfall, the Contracting Officer shall be

notified immediately.

3.5.2 Grounding Connections

Make grounding connections which are buried or otherwise normally inaccessible, by exothermic weld or

compression connector.

- Make exothermic welds strictly in accordance with the weld manufacturer's written

recommendations. Welds which are ·puffed up· or which show convex surfaces indicating improper

cleaning are nor acceptable. Mechanical connectors are not required at exothermic welds.

- Make compression connections using a hydraulic compression tool to provide the correct

circumferential pressure. Tools and dies shall be as recommended by the manufacturer. An

embossing die code or other standard method shall provide visible indication that a connector has

been adequately compressed on the ground wire.

3.5.3 Grounding Conductors

Provide bare grounding conductors, except where installed in conduit with associated phase conductors.

Ground cable sheaths, cable shields, conduit, and equipment with NO.6 AWG. Ground other noncurrent·

carrying metal parts and equipment frames of metal-enclosed equipment. Ground metallic frames and

covers of handholes and pull boxes with a braided, copper ground strap with equivalent ampacity of NO.6

AWG.

3.6 EXCAVATING, BACKFILLING, AND COMPACTING

Provide in accordance with NFPA 70 and Section 02315N EXCAVATION AND FILL.

3.6.1 Reconditioning of Surfaces

3.6.1.1 Unpaved Surfaces

Restore to their original elevation and condition unpaved surfaces disturbed during installation of

duct for direct burial cable. Preserve sod and topsoil removed during excavation and reinstall after

backfilling is completed. Replace sod that is damaged by sod of quality equal to that removed.

When the surface is disturbed in a newly seeded area, re-seed the restored surface with the same

quantity and formula of seed as that used in the original seeding, and provide top-soiling, fertilizing,

liming, seeding, sodding, sprigging, or mulching.

3.7 FIELD QUALITY CONTROL

3.7.1 Performance of Field Acceptance Checks and Tests

Perform in accordance with the manufacturer's recommendations, and include the following visual and

mechanical inspections and electrical tests, performed in accordance with NETA ATS.

3.7.1.1 Medium Voltage Cables

Perform tests after installation of cable, splices, and terminators and before terminating to

equipment or splicing to existing circuits.

- Visual and Mechanical lnspection

  - Inspect exposed cable sections for physical damage.

  - Verify that cable is supplied and connected in accordance

with contract plans and specifications.

  - Inspect for proper shield grounding, cable support, and cable

termination.

  - Verify that cable bends are not less than lCEA or manufacturers minimum allowable

bending radius.

  - Inspect for proper fireproofing.

  - Visually inspect jacket and insulation condition.

  - Inspect for proper phase identification and arrangement.

- Eleclrical Tests

  - Perform a shield continuity test on each power cable by ohmmeter method. Record

ohmic value, resistance values in excess of 10 ohms per 1000 feet of cable must be

investigated and justified.

  - Perform acceptance test on new cables before the new cables are connected to

existing cables and placed into service, including terminations and joints. Perform

maintenance test on complete cable system after the new cables are connected to

existing cables and placed into service, including existing cable, terminations, and joints.

Tests shall be very low frequency (VLF) alternating voltage withstand tests in accordance

with IEEE Std 400.2. VLF test frequency shall be 0.05 Hz minimum for a duration of 60

minutes using a sinusoidal waveform. Test voltages shall be as follows:

CABLE RATING AC TEST VOLTAGE for ACCEPTANCE TESTING

5 KV 		10kV rms(peak)

8 kV		13kV rms(peak)

15kV		20kV rms(peak)

25kV	 	31kV rms(peak)

35 kV 		44kV rms(peak)

3.7.1.2 Grounding System

- Visual and mechanical inspection

Inspect ground system for compliance with contract plans and specifications.

- Electrical tests

Perform ground-impedance measurements utilizing the fall-of-potential method in

accordance with IEEE STD 81. On systems consisting of interconnected ground rods,

perform tests after interconnections are complete. On systems consisting of a single

ground rod perform tests before any wire is connected. Take measurements in normally

dry weather, not less than 48 hours after rainfall. Use a portable megohmmeter tester in

accordance with manufacturer's instructions to test each ground or group of grounds. The

instrument shall be equipped with a meter reading directly in ohms or fractions thereof to

indicate the ground value of the ground rod or grounding systems under test.

3.7.2 Follow-Up Verification

Upon completion of acceptance checks and tests, the Contractor shall show by demonstration in

service that circuits and devices are in good operating condition and properly performing the

intended function. As an exception to requirements stated elsewhere in the contract, the

Contracting Officer shall be given 5 working days advance notice of the dates and times of

checking and testing .

END OF SECTION