SECTION 10200 - LOUVERS AND VENTS

- GENERAL

      - SECTION REQUIREMENTS

Delete paragraph below if performance requirements are not needed.

        - Provide louvers complying with performance requirements indicated as demonstrated by testing according to AMCA 500.

Usually delete Shop Drawings in paragraph below for uncomplicated projects.

        - Submittals:  Product Data, Shop Drawings showing elevations and details including profiles, angles, and spacing of louver blades; free area; and anchorage details, and Samples showing the full range of colors available for units with factory-applied color finishes.

- PRODUCTS

      - MATERIALS

        - Aluminum Extrusions:  ASTM B 221 (ASTM B 221M), alloy 6063-T5 or T-52.

        - Aluminum Sheet:  ASTM B 209 (ASTM B 209M), alloy 3003 or 5005.

        - Galvanized Steel Sheet:  ASTM A 653/A 653M, G90 (Z275) zinc coating, mill phosphatized.

        - Stainless-Steel Sheet:  ASTM A 666, Type 302 or 304.

        - Fasteners:  Of same basic metal and alloy as fastened metal or 300 Series stainless steel.

      - LOUVERS

Retain paragraph below for performance specification for extruded-aluminum louvers.

        - Horizontal extruded-aluminum louvers, with either drainable or nondrainable fixed blades, and complying with the following:

          - Louver Depth:  2 inches (50 mm).

          - Frame and Blade Thickness: 0.081 inch (2.06 mm).

Values in subparagraph below are examples only; select one and revise to suit Project.  First applies to high-performance, drainable-blade louvers; second, to most drainable-blade and some plain-blade louvers; and third, to most plain and baffle-type blade louvers.

          - Performance Requirements:  Not less than 8500 cfm (4010 L/s) with not more than 0.20-inch wg (50-Pa) static-pressure loss for units 48 inches (1220 mm) wide by 48 inches (1220 mm) high.

          - Water Penetration:  Not more than 0.01 oz./sq. ft. (3.1 g/sq. m) of free area at above airflow rate.

Retain paragraph below for descriptive specification for extruded-aluminum louvers.

Retain paragraph below for performance specification for formed-metal louvers.

        - Horizontal formed-metal louvers, with either drainable or nondrainable fixed blades, and complying with the following:

          - Louver Depth: 4 inches (100 mm).

          - Metal and Thickness:  Galvanized steel sheet, 0.064 inch (1.6 mm).

Values in subparagraph below are examples only; select one and revise to suit Project.  First applies to most drainable-blade louvers; second, to most plain and baffle-type blade louvers.

          - Performance Requirements:  Not less than 7300 cfm (3440 L/s) with not more than 0.12-inch wg (30-Pa) static-pressure loss for units 48 inches (1220 mm) wide by 48 inches (1220 mm) high.

          - Water Penetration:  Not more than 0.01 oz./sq. ft. (3.1 g/sq. m) of free area at above airflow rate.

Retain paragraph below for descriptive specification for formed-metal louvers.

      - LOUVER SCREENS

        - On exterior face of exterior louvers provide louver screens with rewireable frames of same kind and form of metal as louvers.

          - Bird screening made from aluminum or stainless-steel wire at aluminum louvers.

          - Bird screening made from galvanized steel wire at galvanized steel louvers.

      - FINISHES

        - Conversion-coated and factory-primed finish, AA-C12C42R1x, on aluminum louvers.

        - Class I, clear anodic finish; AA-M12C22A41; complying with AAMA 607.1; on aluminum louvers.

        - Class I, color anodic finish; AA-M12C22A42/A44; complying with AAMA 606.1 or AAMA 608.1; on aluminum louvers.

        - Baked-enamel finish, AA-C12C42R1x, on aluminum louvers.  Use thermosetting, modified-acrylic enamel primer/topcoat system complying with AAMA 603.8.

        - High-performance organic coating finish, AA-C12C42R1x, on aluminum louvers.  Use manufacturer's standard 3-coat fluoropolymer system complying with AAMA 605.2, with finish coats containing at least 70 percent polyvinylidene fluoride resin by weight.

        - Factory-primed finish on galvanized steel louvers for field painting.  Clean and apply conversion coating followed by air-dried primer.

        - Baked-enamel finish on galvanized steel louvers.  Use thermosetting, modified-acrylic enamel primer/topcoat system applied over cleaned and conversion-coated metal.

        - No. 4 finish on stainless steel louvers.

- EXECUTION

      - INSTALLATION

        - Install louvers level, plumb, and at indicated alignment with adjacent work.

        - Use concealed anchorages where possible.

        - Protect metal surfaces from corrosion or galvanic action by applying a heavy coating of bituminous paint on surfaces that will be in contact with concrete, masonry, or dissimilar metals.

END OF SECTION 10200