SECTION 16520 · EXTERIOR LUMINAIRES

PARTl GENERAL

1.1 SECTION INCLUDES

- Exterior luminaires and accessories.

1.2 REFERENCES

- ANSI C78.379 • American National Standard for Electric lamps .. Reflector Lamps -- Classification of

Beam Patterns; 2006.

- ANSI C82.1 • American National Standard for Lamp Ballast· Line Frequency Fluorescent Lamp

Ballast; 2004.

- ANSI C82.4 - American National Standard for Ballasts for High-Intensity-Discharge and Low Pressure

Sodium Lamps (Multiple·Supply Type); 2002.

- NECA/IESNA 501 . Recommended Practice for Installing Exterior lighting Systems; 2006.

- NFPA 70 - National Electrical Code, National Fire Protection Association (Edition Adopted by

Authority Having Jurisdiction).

1.3 SUBMITIALS

- Product Data (including photocells, timers, and lighting contactors): Provide dimensions, ratings, and

performance data.

1,4 QUAlI1Y ASSURANCE

- Conform to requirements 01 NFPA 70.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this

section with minimum three years documented experience.

- Electrical Components: Listed and classified by Underwriters Laboratories Inc. as suitable for the

purpose specified and indicated.

PART 2 PRODUCTS

2.1 LUMINAIRES

- Furnish products as indicated in Schedule included on the Drawings. For substitutions, see Section

16050. Confirm mounting, type, voltage and wattage is correct before ordering.

2.2 BALLASTS

- Fluorescent Ballasts: ANSI C82.1, high power factor type electromagnetic ballast, suitable for lamps

specified.

  - Provide low-temperature ballast suitable for lamps specified.

  - Voltage: Match luminaire voltage.

- High Intensity Discharge (HID) Ballasts: ANSI C82.4, metal halide or high pressure sodium lamp

ballast (as indicated in schedule on drawings), suitable for lamp specified.

1. Voltage: Match luminaire voltage.

2.3 TIME-SWITCHES AND OTHER LIGHTING CONTROL

- Time switch controls shall be as noted on the Drawings and shall be multi-pole, Single throw, rated 20

amperes per pole (minimum), with astronomic dial properly selected for latitude of installation and 16

hour (minimum) spring reserve carry-over in event of power failure. Time switch shall be in NEMA 3R

surface mounted enclosure unless otherwise noted.

- Lighting contactors shall be meet NEMA ICS and shall be electrically held. Contacts shall be rated as

indicated.

- Photocells shall be hermetically sealed cadmium-sulfide or silicon diode type cell rated tor voltage of

fixtures used with a minimum of 240 volts AC. Switch shall turn on at or below 3 foot-candles and off at

2 to 10 foot-candles. A time delay shall prevent accidental switching from transient light sources.

PART3 EXECUTION

3.1 INSTALLATION

- Install fixtures securely, in a neat and workmanlike manner, as specified in NECA 50l.

- Install lamps in each luminaire.

- Bond luminaires, metal accessories, and metal poles to branch circuit equipment grounding

conductor. Provide supplementary grounding electrode at each pole.

3.2 FIELD QUALITY CONTROL

- Operate each luminaire after installation and connection. Inspect for improper connections and

operation.

3.3 CLEANING

- Clean electrical parts to remove conductive and deleterious materials.

- Remove dirt and debris from enclosure.

- Clean photometric control surfaces as recommended by manufacturer.

- Clean finishes and touch up damage.

3.4 PROTECTION OF FINISHED WORK

- Re-lamp luminaires that have failed lamps at Substantial Completion.

3.5 SCHEDULE - See Drawings

END OF SECTION