SECTION 16411 . ENCLOSED CIRCUIT BREAKERS

PART 1 GENERAL

  - SECTION INCLUDES

- Enclosed circuit breakers.

1.2 REFERENCES

- NECA (INST)· NECA Standard of Installation; National Electrical Contractors Association; 1993.

- NEMA AS 1 • Molded Case Circuit Breakers and Molded Case Switches; National Electrical

Manufacturers Association; 1993.

- NFPA 70 . National Electrical Code; National Fire Protection Association (edition adopted by

Authority Having Jurisdiction).

1.3 SUBMITTALS

- See Section 01300 • Administrative Requirements, for submittal procedures.

- Product Data: Provide catalog sheets showing ratings, trip units, time current curves, dimensions,

and enclosure details.

1.4 OUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Perform Work in accordance with NECA Standard of Installation.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this

section with minimum three years documented experience.

- Products: Furnish products listed and classified by Underwriters Laboratories Inc. as suitable for

purpose specified and indicated.

PART 2 PRODUCTS

2.1 MANUFACTURERS

- Basis of Design: Square D; www.squared.com.

2.2 MOLDED CASE CIRCUIT BREAKERS

- Circuit Breakers: NEMA AB 1.

2.3 ACCESSORIES

- Enclosures:

- Finish: Manufacturer's standard enamel finish, gray color.

- Provide accessories as scheduled.

- Provide products suitable for use as service entrance equipment where so applied.

PART 3 EXECUTION

3.1 INSTALLATION

- Install enclosed circuit breakers where indicated, in accordance with manufacturer's instructions.

- Install enclosed circuit breakers plumb. Provide supports in accordance with Section 16070.

- Height: 5 feet (1.6 M) to operating handle.

- Provide engraved plastic nameplates under the provisions of Section 16075.

3.2 FIELD QUALITY CONTROL

- Inspect and test each circuit breaker.

- Inspect each circuit breaker visually.

- Perform several mechanical ON-OFF operations on each circuit breaker.

- Verify circuit continuity on each pole in closed position.

- For circuit breakers 600A or larger, determine that circuit breaker will trip on over-current condition,

with tripping time to NEMA AB 1 requirements. Include description of testing and results in lest report

END OF SECTION