SECTION 15183 - REFRIGERANT PIPING

- GENERAL

      - SECTION REQUIREMENTS

        - Submittals:  Shop drawings indicating oil traps, double risers, specialties, and pipe and tube sizes.

        - Comply with ASME B31.5, "Refrigerant Piping" and ASHRAE 15, "Safety Code for Mechanical Refrigeration."

- PRODUCTS

      - PIPES AND TUBES

        - Hard Copper Tube:  ASTM B 280, Type ACR, drawn temper.

        - Soft Copper Tube:  ASTM B 280, Type ACR, annealed temper.

      - FITTINGS

        - Copper Fittings:  ASME B16.22, wrought-copper streamlined pattern.

      - JOINING MATERIALS

        - Brazing Filler Metals:  AWS A5.8, Classification BAg-1 (Silver).

      - VALVES

        - Minimum Pressure and Temperature Ratings:  500-psig (3450-kPa) working pressure and 275 deg F (135 deg C) working temperature, unless otherwise indicated.

        - Thermal-Expansion Valves:  Comply with ARI 750; with sensing bulb, distributor having side connection for hot-gas bypass line, and external equalizer line.

      - REFRIGERANT PIPING SPECIALTIES

        - Moisture/Liquid Indicators:  500-psig (3450-kPa) operating pressure, 200 deg F (93 deg C) operating temperature, with replaceable, polished, optical viewing window with color-coded moisture indicator.

        - Refrigerant:  ASHRAE 34.

- EXECUTION

      - INSTALLATION

        - Install refrigerant piping according to ASHRAE 15, and as recommended by the equipment manufacturer.

        - Basic piping installation requirements are specified in Division 15 Section "Common Piping Requirements."

        - Belowground, install copper tubing in conduit.  Vent conduit outdoors.

        - Insulate  liquid lines.

        - Charge and purge systems, after testing, and dispose of refrigerant by following ASHRAE 15 procedures.

        - Install refrigerant charging (packed angle) valve in liquid line between receiver shutoff valve and expansion valve.

        - Install globe valves on each side of strainers and dryers, in liquid and suction lines at evaporators, and elsewhere as indicated.

        - Install solenoid valves ahead of each expansion valve and hot-gas bypass valve.  Install solenoid valves in horizontal lines with coil at top.

        - Install liquid indicators in liquid line leaving condenser, in liquid line leaving receiver, and on leaving side of liquid solenoid valves.

        - Install moisture/liquid indicators in liquid lines between filter dryers and thermostatic-expansion valves and in liquid line to receiver.

END OF SECTION 15183