SECTION 07710 - MANUFACTURED ROOF SPECIALTIES

- GENERAL

      - SECTION REQUIREMENTS

        - Submittals: Product Data, Shop Drawings, and color Samples.

        - Provide products that comply with applicable requirements of SMACNA's "Architectural Sheet Metal Manual," unless otherwise indicated.

- PRODUCTS

      - ROOF SPECIALTIES

        - Coil-Coated Galvanized Steel Gutters and Downspouts.

        - Aluminum Extrusions: ASTM B 221 (ASTM B 221M), 6063-T5 alloy and temper, or as recommended by manufacturer for use intended and as required for proper application of finish indicated.

Retain first alloy and thickness in paragraph below for mill finish aluminum; retain second alloy and thickness for coated aluminum.

        - Aluminum Sheet: ASTM B 209 (ASTM B 209M), 3003-H14 alloy and temper, or as recommended by manufacturer for use intended and as required for proper application of finish indicated, with a minimum thickness of 0.050 inch (1.2 mm).

        - Aluminum Finish: Mill finish, AAM10, high-performance coating, AAC12C42R1X, composed of inhibitive primer and color topcoat containing not less than 70 percent polyvinylidene fluoride resin by weight, with a total minimum dry film thickness of 0.9 mil (0.023 mm); complying with AAMA 1402, Test Method No. 7.

        - Coil-Coated Galvanized Steel Sheet: Galvanized steel sheet, ASTM A 653/A 653M, G90 (Z275), 0.028 inch (0.7 mm) thick,; prepainted with 2-coat fluoropolymer according to ASTM A 755 (ASTM A 755M), composed of inhibitive primer and color topcoat containing not less than 70 percent polyvinylidene fluoride resin by weight, with a total minimum dry film thickness of 0.9 mil (0.023 mm).

- EXECUTION

      - INSTALLATION

        - Coordinate with installation of roof decks and other substrates to produce a watertight assembly capable of withstanding inward and outward loading pressures, and thermal and lateral loads.

        - Coat back side of steel roof specialties with bituminous coating where they will contact wood, ferrous metal, or cementitious construction.

        - Expansion Provisions: Install running lengths to allow controlled expansion for movement of metal components, to prevent water leakage, deformation, or damage.

END OF SECTION 07710