SECTION 07411 - METAL ROOF PANELS

- GENERAL

      - SECTION REQUIREMENTS

        - Submittals: Product Data, Shop Drawings, and color Samples.

Delete paragraph below if not required or not available for roof panels selected.

        - Provide roof assemblies that meet requirements of UL 580 for Class 90 wind-uplift resistance.

        - Submit a written warranty, executed by manufacturer, agreeing to repair or replace metal roof panels that fail to remain weathertight within five years from date of Substantial Completion.

- PRODUCTS

      - METAL ROOF PANELS

        - Galvanized Steel Roof Panels: Fabricated from galvanized structural steel sheet, ASTM A 653/A 653M, G90 (Z275); 0.034 inch (0.85 mm) thick.

        - Factory finish panel material by coil coating with 2-coat fluoropolymer according to ASTM A 755 (ASTM A 755M), composed of inhibitive primer and color topcoat containing not less than 70 percent polyvinylidene fluoride resin by weight, with a total minimum dry film thickness of 0.9 mil (0.023 mm).

        - Roof Panel Assembly: Batten seam.

      - ACCESSORIES

        - Provide all components required for a complete roof panel assembly including trim, fasciae, clips, seam covers, flashings, sealants, gaskets, fillers, closure strips, and similar items.

        - Underlayment: Self-adhering, polymer-modified, bituminous sheet ASTM D 1970; 40 mils (1 mm) thick.

        - Bituminous Coating: Cold-applied asphalt mastic, SSPC-Paint 12, compounded for 15-mil (0.4-mm) dry film thickness per coat.

- EXECUTION

      - INSTALLATION

        - Anchor panels securely in place, with provisions for thermal and structural movement.  Field cutting exterior panels by torch is not permitted.  Install panels with concealed fasteners, unless otherwise indicated.

        - Separate dissimilar metals with a bituminous coating or rubberized-asphalt underlayment.

        - Coat back side of steel panels with bituminous coating where they will contact wood, ferrous metal, or cementitious construction.

END OF SECTION 07411