SECTION 16131 - CONDUIT

PART 1 GENERAL

1.1 SECTION INCLUDES

- Conduit, fittings and conduit bodies.

1.2 REFERENCES

- ANSI C80.1 - American National Standard for Electrical Rigid Steel Conduit (ERSC); 2005.

- ANSI C80.3 - American National Standard for Steel Electrical Metallic Tubing (EMT); 2005.

- ANSI C80.5 - American National Standard for Electrical Rigid Aluminum Conduit (ERAC); 2005.

- NECA 1 - Standard Practices for Good Workmanship in Electrical Contracting; National Electrical

Contractors Association; 2006.

- NECA 101 - Standard for Installing Steel Conduit (Rigid, IMC, EMT); National Electrical Contractors

Association; 2006.

- NEMA FB 1 - Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit, Electrical Metallic Tubing,

and Cable; National Electrical Manufacturers Association; 2007.

- NEMA RN 1 - Polyvinyl Chloride (PVC) Externally Coated Galvanized Rigid Steel Conduit and

Intermediate Metal Conduit; National Electrical Manufacturers Association; 2005.

- NEMA TC 2 - Electrical Polyvinyl Chloride (PVC) Tubing and Conduit; National Electrical

Manufacturers Association; 2003.

- NEMA TC 3 - PVC Fittings for use with Rigid PVC Conduit and Tubing; National Electrical

Manufacturers Association; 2004.

- NFPA 70 - National Electrical Code, National Fire Protection Association (edition adopted by Authority

Having Jurisdiction).

1.3 QUALITY ASSURANCE

- Conform to requirements of NFPA 70.

- Products: listed and classified by Underwriters Laboratories Inc. as suitable for purpose specified and

shown.

1.4 DELIVERY, STORAGE, AND HANDLING

- Accept conduit on site. Inspect for damage.

- Protect conduit from corrosion and entrance of debris by storing above grade. Provide appropriate

covering.

- Protect PVC conduit from sunlight.

PART 2 PRODUCTS

2.1 CONDUIT REQUIREMENTS

- Conduit Size: Comply with NFPA 70.

- Minimum Size: 1/2 inch (13 mm) unless otherwise specified. This minimum size does not

apply to flexible conduit.

2.2 METAL CONDUIT

- Rigid Steel Conduit: ANSI C80.1.

- Rigid Aluminum Conduit: ANSI C8O.5.

- Fittings and Conduit Bodies: NEMA FB 1; material to match conduit.

2.3 PVC COATED METAL CONDUIT

- Description: NEMA RN 1; rigid steel conduit with external PVC coating.

- Description: NEMA RN 1; rigid steel conduit with external PVC coating, 20 mil (0.05 mm) thick.

- Fittings and Conduit Bodies: NEMA FB 1; steel fittings with external PVC coating to match conduit.

2.4 FLEXIBLE METAL CONDUIT

- Description: Interlocked steel construction.

- Fittings: NEMA FB 1.

2.5 LlQUIDTIGHT FLEXIBLE METAL CONDUIT

- Description: Interlocked steel construction with PVC jacket.

- Fittings: NEMA FB 1.

2.6 ELECTRICAL METALLIC TUBING (EMT)

- Description: ANSI C80.3; galvanized tubing.

- Fittings and Conduit Bodies: NEMA FB 1; steel or malleable iron compression type.

2.7 NONMETALLIC CONDUIT

- Description: NEMA TC 2; Schedule 40 PVC.

- Fittings and Conduit Bodies: NEMA TC 3.

PART 3 EXECUTION

3.1 EXAMINATION

- Verify routing and termination locations of conduit prior to rough in.

3.2 INSTALLATION

- Install conduit securely, in a neat and workmanlike manner, as specified in NECA 1.

- Install steel conduit as specified in NECA 101.

- All wiring shall be in conduit. Routing of conduit shown on drawings is intended to be diagrammatic

and where changes are necessary as a result of structural conditions, apparatus, or other causes,

routing shall be changed to meet conditions. Conduit risers and offsets are not indicated on

drawings, but are intended to be installed as required. Conduit shall be selected according to

location and code requirements.

- EMT shall be used in the building interior up to 2" in diameter unless otherwise indicated. EMT

conduit shall not be used in wet or hazardous locations, below grade or in concrete.

- Liquid-tight flexible metal conduit shall be used for final connections to motors, appliances and

vibrating equipment and shall be a maximum of six feet in length (regular flexible metal conduit may

be used for final connection to interior light fixtures).

- MC Cable shall only be used in walls for concealed, interior 15A and 20A, 120V branch circuits,

Homeruns for these circuits shall be in EMT conduit.

- Flexible Metal Conduit shall only be used for final connection to equipment (non vibrating) with a

maximum length of six feet (four feet for plenum ceilings). Nonmetallic flex conduit or tubing shall not

be used.

- Galvanized rigid conduit shall be used for incoming feeder to all the panels.

- Underground conduit or conduit in concrete shall be PVC Schedule 40 (Type-EPC) or PVC coated

rigid steel unless indicated otherwise. Conduit under slab-on-grade shall be buried at least 12" below

the vapor barrier. Per the Standard Building Code, conduit embedded in concrete slabs, walls, or

beams shall not have an outside dimension more than one-third the overall thickness of the concrete

in which they are imbedded. Conduit shall not be run lengthwise in footings. Transitions to

above ground shall be made with PVC coaled rigid steel or with rigid steel conduit coated with 2 coats

of asphaltic mastic. PVC conduit shall not be used aboveground.

- Per NEC paragraph 300.5, provide warning tape or ribbon 12" below grade for a service lateral

conduit that is not encased in concrete.

- All metallic conduit terminating in outlet, junction or pull boxes and cabinets must terminate with

bushing and double locknuts except exposed cast boxes, where they may be omitted. Conduit sizes

1·1/4” and above shall have insulating fiber bushings with double locknuts. Grounding type bushings

must be used at points where grounding continuity is broken and at service entrance equipment.

EMT conduit shall have compression type fittings (set screw connectors are not acceptable).

- Install nonmetallic conduit in accordance with manufacturer's instructions.

- Arrange supports to prevent misalignment during wiring installation.

- Support conduit using coated steel or malleable iron straps, lay-in adjustable hangers, clevis hangers,

and split hangers.

- Group related conduits; support using conduit rack. Construct rack using steel channel; provide

space on each for 25 percent additional conduits.

- Fasten conduit supports to building structure and surfaces under provisions of Section 16070.

- Do not support conduit with wire or perforated pipe straps. Remove wire used for temporary supports.

- Do not attach conduit to ceiling support wires.

- Arrange conduit to maintain headroom and present neat appearance.

- Route exposed conduit parallel and perpendicular to walls. Do not run conduit exposed in occupied

areas unless noted otherwise.

- Route conduit installed above accessible ceilings parallel and perpendicular to walls.

- Route conduit in and under slab from point-to-point.

- Do not cross conduits in slab.

- Maintain adequate clearance between conduit and piping.

- Maintain 12 inch (300 mm) clearance between conduit and surfaces with temperatures exceeding

104 degrees F (40 degrees C).

- Cut conduit square using saw or pipecutter; de-burr cut ends.

- Bring conduit to shoulder of fittings; fasten securely.

- For conduit installed in floors that are in place before conduit is installed, properly seal around

conduit, including any required fire chalk.

- Install no more than equivalent of four 90 degree bends between boxes. Use conduit bodies to make

sharp changes in direction, as around beams. Use hydraulic one shot bender to fabricate bends in

metal conduit larger than 2 inch (50 mm) size.

- Avoid moisture traps; provide junction box with drain fitting at low points in conduit system.

- Provide suitable fittings to accommodate expansion and deflection where conduit crosses seismic

and expansion joints complete with copper bonding jumper.

- Provide suitable pull string in each empty conduit except sleeves and nipples.

- Use suitable caps to protect installed conduit against entrance of dirt and moisture.

- Ground and bond conduit under provisions of Section 16060.

- In wooden load-bearing and exterior walls, do not cut or notch any wooden framing member to a

depth exceeding 25 percent of its width. For wooden nonload-bearing walls, do not cut or notch any

wooden framing member to a depth exceeding 40 percent of its width.

3.3 INTERFACE WITH OTHER PRODUCTS

- Install conduit to preserve fire resistance rating of partitions and other elements using materials and

methods listed as part of UL system.

- Route conduit through roof openings for piping and ductwork wherever possible. Where separate

roofing penetration is required, coordinate location and installation method with roofing installation.

END OF SECTION